## Sheet1
SCHEDULE OF QUANTITIES FOR FIRE PROTECTION SYSTEM
S.NO | Group | Sub Group 1 | Sub Group 2 | Item Name | DESCRIPTION | QTY | UNIT | RATE | AMOUNT | REMARKS
1 | HYDRANTS, PIPING AND ACCESSORIES |  |  | 200 mm dia | Providing and fixing black steel pipes conforming to IS: 3589 (6mm thick) with accessories including all fittings like tees, elbows reducers, flanges, rubber gaskets, GI nuts, bolts and washers. And hangers, clamp supports from walls, floors and ceiling including cutting holes and chases in brick work, making good the same to original condition complete in all respects.Incluiding painting as per item no 3. | QR | RM | 4857
1.1 | HYDRANTS, PIPING AND ACCESSORIES |  |  | 250 mm dia | a) 200 mm dia | QR | RM | 6053
1.2 | HYDRANTS, PIPING AND ACCESSORIES |  |  | 300 mm dia | b) 250 mm dia | QR | RM | 7190
2 | HYDRANTS, PIPING AND ACCESSORIES | MS Class |  | 20 mm dia | Providing, laying, jointing, testing and commissioning of following sizes of MS C class pipes conforming to IS-1239 with all type of fittings like tees, elbows, reducers, union, flanges, rubber & gaskets with welded joints above 50mm dia and DI threaded fittings shall be used for 50mm dia and below, GI nuts bolts, washer including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. G.I. pipe sleeve of one size larger diameter shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Manager’s / Consultants requirements including cutting holes and chases in brick work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets, I section, channel, etc. shall be of galvanized iron and then supply of the same shall also be included for rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted. | QR | RM | 450
| HYDRANTS, PIPING AND ACCESSORIES | MS Class |  | 25 mm dia | Providing, laying, jointing, testing and commissioning of following sizes of MS C class pipes conforming to IS-1239 with all type of fittings like tees, elbows, reducers, union, flanges, rubber & gaskets with welded joints above 50mm dia and DI threaded fittings shall be used for 50mm dia and below, GI nuts bolts, washer including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. G.I. pipe sleeve of one size larger diameter shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Manager’s / Consultants requirements including cutting holes and chases in brick work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets, I section, channel, etc. shall be of galvanized iron and then supply of the same shall also be included for rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted. | 8290 | RM | 615 | 5098350
| HYDRANTS, PIPING AND ACCESSORIES | MS Class |  | 32 mm dia | Providing, laying, jointing, testing and commissioning of following sizes of MS C class pipes conforming to IS-1239 with all type of fittings like tees, elbows, reducers, union, flanges, rubber & gaskets with welded joints above 50mm dia and DI threaded fittings shall be used for 50mm dia and below, GI nuts bolts, washer including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. G.I. pipe sleeve of one size larger diameter shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Manager’s / Consultants requirements including cutting holes and chases in brick work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets, I section, channel, etc. shall be of galvanized iron and then supply of the same shall also be included for rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted. | 1045 | RM | 800 | 836000
| HYDRANTS, PIPING AND ACCESSORIES | MS Class |  | 40 mm dia | Providing, laying, jointing, testing and commissioning of following sizes of MS C class pipes conforming to IS-1239 with all type of fittings like tees, elbows, reducers, union, flanges, rubber & gaskets with welded joints above 50mm dia and DI threaded fittings shall be used for 50mm dia and below, GI nuts bolts, washer including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. G.I. pipe sleeve of one size larger diameter shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Manager’s / Consultants requirements including cutting holes and chases in brick work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets, I section, channel, etc. shall be of galvanized iron and then supply of the same shall also be included for rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted. | 840 | RM | 900 | 756000
| HYDRANTS, PIPING AND ACCESSORIES | MS Class |  | 50 mm dia | Providing, laying, jointing, testing and commissioning of following sizes of MS C class pipes conforming to IS-1239 with all type of fittings like tees, elbows, reducers, union, flanges, rubber & gaskets with welded joints above 50mm dia and DI threaded fittings shall be used for 50mm dia and below, GI nuts bolts, washer including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. G.I. pipe sleeve of one size larger diameter shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Manager’s / Consultants requirements including cutting holes and chases in brick work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets, I section, channel, etc. shall be of galvanized iron and then supply of the same shall also be included for rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted. | 800 | RM | 1000 | 800000
| HYDRANTS, PIPING AND ACCESSORIES | MS Class |  | 65 mm dia | Providing, laying, jointing, testing and commissioning of following sizes of MS C class pipes conforming to IS-1239 with all type of fittings like tees, elbows, reducers, union, flanges, rubber & gaskets with welded joints above 50mm dia and DI threaded fittings shall be used for 50mm dia and below, GI nuts bolts, washer including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. G.I. pipe sleeve of one size larger diameter shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Manager’s / Consultants requirements including cutting holes and chases in brick work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets, I section, channel, etc. shall be of galvanized iron and then supply of the same shall also be included for rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted. | 650 | RM | 1200 | 780000
| HYDRANTS, PIPING AND ACCESSORIES | MS Class |  | 80 mm dia | Providing, laying, jointing, testing and commissioning of following sizes of MS C class pipes conforming to IS-1239 with all type of fittings like tees, elbows, reducers, union, flanges, rubber & gaskets with welded joints above 50mm dia and DI threaded fittings shall be used for 50mm dia and below, GI nuts bolts, washer including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. G.I. pipe sleeve of one size larger diameter shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Manager’s / Consultants requirements including cutting holes and chases in brick work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets, I section, channel, etc. shall be of galvanized iron and then supply of the same shall also be included for rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted. | 1070 | RM | 1500 | 1605000
| HYDRANTS, PIPING AND ACCESSORIES | MS Class |  | 100 mm dia | Providing, laying, jointing, testing and commissioning of following sizes of MS C class pipes conforming to IS-1239 with all type of fittings like tees, elbows, reducers, union, flanges, rubber & gaskets with welded joints above 50mm dia and DI threaded fittings shall be used for 50mm dia and below, GI nuts bolts, washer including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. G.I. pipe sleeve of one size larger diameter shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Manager’s / Consultants requirements including cutting holes and chases in brick work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets, I section, channel, etc. shall be of galvanized iron and then supply of the same shall also be included for rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted. | 760 | RM | 1800 | 1368000
| HYDRANTS, PIPING AND ACCESSORIES | MS Class |  | 150 mm dia | Providing, laying, jointing, testing and commissioning of following sizes of MS C class pipes conforming to IS-1239 with all type of fittings like tees, elbows, reducers, union, flanges, rubber & gaskets with welded joints above 50mm dia and DI threaded fittings shall be used for 50mm dia and below, GI nuts bolts, washer including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. G.I. pipe sleeve of one size larger diameter shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Manager’s / Consultants requirements including cutting holes and chases in brick work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets, I section, channel, etc. shall be of galvanized iron and then supply of the same shall also be included for rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted. | 2150 | RM | 2500 | 5375000
| HYDRANTS, PIPING AND ACCESSORIES | MS Class |  | 200 mm dia | Providing, laying, jointing, testing and commissioning of following sizes of MS C class pipes conforming to IS-1239 with all type of fittings like tees, elbows, reducers, union, flanges, rubber & gaskets with welded joints above 50mm dia and DI threaded fittings shall be used for 50mm dia and below, GI nuts bolts, washer including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. G.I. pipe sleeve of one size larger diameter shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Manager’s / Consultants requirements including cutting holes and chases in brick work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets, I section, channel, etc. shall be of galvanized iron and then supply of the same shall also be included for rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted. | 50 | RM | 4398 | 219900