## BOQ DNM PLUMBING
BOQ OF QUANTITIES MARRIOTT HOTEL
S.NO | Group | Sub Group 1 | Sub Group 2 | Item Name | DESCRIPTION | QTY | UNIT | RATE | AMOUNT | REMARKS
1 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of European water closet,(a) C.P. bolts and nuts(b) C.I. chair, or other hanging arrangements by Fischer / Hilti (c) Bakelite toilet seat and cover, Water closet as described above | Receiving, shifting, installing and testing of vitreous china wall / floor mounting type European water closet & the followings complete with all accessories. Including cutting the walls & R.C.C floor slabs making good the same complete as required.(a) C.P. bolts and nuts(b) C.I. chair, or other hanging arrangements by Fischer / Hilti (c) Bakelite toilet seat and cover, Water closet as described above | 233 | NOS | 750 | 174750
2 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of concealed type dual flushing cistern, (a) Flush actuator facia assembly including brass / SS screws(b) Bush and washer(c) Heavy class PVC flush pipe upto cistern including connection to WC(d)Angle valve with flexible connection.Flushing cistern as described above | Receiving, shifting, installing and testing of concealed type dual flushing cistern of with adjustment of 3 - 4.5 litres with the following complete. The flush pipe shall be concealed in wall and connected to the WC with required fittings. Cutting the wall and making good same complete as required (a) Flush actuator facia assembly including brass / SS screws(b) Bush and washer(c) Heavy class PVC flush pipe upto cistern including connection to WC(d)Angle valve with flexible connection.Flushing cistern as described above | 233 | NOS | 450 | 104850
3 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of handicap toilet | Receiving, shifting, installing and testing of 2 Nos. support arms and backrest to mount at fixed height for handicap toilet complete as required. | 4 | SET | 400 | 1600
4 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of handicap toilet(Model R-35: Presalit – Commander) | Receiving, shifting, installing and testing of raised toilet seat with cover for handicap toilet(Model R-35: Presalit – Commander) | 4 | NOS | 300 | 1200
5 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of CP Brass Rinsing spray, (a)Regulated of approved quality(b) 1.5m long plastic NBR braided pipe(c) Flexible pipe(d) Wall hooked(e)C.P. Brass angle valve, CP Brass Rinsing spray as described above | Receiving, shifting, installing and testing of CP Brass Rinsing spray with the following complete as required.(a) Regulated of approved quality(b) 1.5m long plastic NBR braided pipe(c) Flexible pipe(d) Wall hooked(e)C.P. Brass angle valve, CP Brass Rinsing spray as described above | 233 | NOS | 110 | 25630
6 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of counter top/below ova/ flat wash basin,(a) C.I. bracket painted white(b) 32mm dia C.P. brass waste(c) C.P. brass chain with rubber plug(d) 32 mm dia C.P. brass bottle trap with extension piece(e) Wall flanges and rubber adapters for waste connection,Wash basin as described above | Receiving, shifting, installing and testing of vitreous china counter top/below ova/ flat wash basin with following complete including cutting and making good the walls floors complete as required.(a) C.I. bracket painted white(b) 32mm dia C.P. brass waste(c) C.P. brass chain with rubber plug(d) 32 mm dia C.P. brass bottle trap with extension piece(e) Wall flanges and rubber adapters for waste connection,Wash basin as described above | 230 | NOS | 600 | 138000
7 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of brackets, tracks (Model R4140) with flexible feed & waste pipes for adjustable type wash basin | Receiving, shifting, installing and testing of brackets, tracks (Model R4140) with flexible feed & waste pipes for adjustable type wash basin complete as required. (Make : Presalit – Commander) | 4 | NO | 800 | 3200
8 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of wash basin complete recessed at the back for the reception | Receiving, shifting, installing and testing of vitreous china pedestal for wash basin complete recessed at the back for the reception of pipes and fittings. | 4 | NOS | 800 | 3200
9 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of C.P. brass basin mixer, (a) 375 mm long copper connection (b) Brass nuts,Basin mixer as described above | Receiving, shifting, installing and testing of C.P. brass basin mixer with the following 375 mm long copper connection, brass nuts and pop up waste complete as required.(a) 375 mm long copper connection (b) Brass nuts,Basin mixer as described above | 230 | NOS | 250 | 57500
10 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of C.P. brass waste with dome type grating | Receiving, shifting, installing and testing of viterous china large flat back urinal supported by CI/MS bracket including C.P. brass waste with dome type grating, C.P.cast brass bottle trap with extension piece,wall flanges complete as required. | 34 | NOS | 800 | 27200
11 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of urinal flushing systems for urinal,(a) Plumbing, electronic and electrical items(b)C.P. brass flush pipe with clamps and screw (c) C.P. brass elbow(d)C.P. brass spreader(e)C.P. wall flange(f) Infra red photo cells(g)solenoid valve,Automatic urinal flushing system as described above | Receiving, shifting, installing and testing of electrically operated (wall burial type) automatic urinal flushing systems for urinal, flushing only when in use, comprising of following complete as required (without any provision required in false ceiling and shaft for solenoid valve).(a) Plumbing, electronic and electrical items(b)C.P. brass flush pipe with clamps and screw (c) C.P. brass elbow(d)C.P. brass spreader(e)C.P. wall flange(f) Infra red photo cells(g)solenoid valve,Automatic urinal flushing system as described above | 34 | NOS | 800 | 27200
12 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of urinal partition of concealed C.I. bracket. | Receiving, shifting, installing and testing of viterous china large urinal partition of concealed C.I. bracket. | 30 | NOS | 600 | 18000
13 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of bath tub (size as per drawing) completely leveled, including waste overflow set | Receiving, shifting, installing and testing of bath tub (size as per drawing) completely leveled, including waste overflow set, chain plug, cast brass P/S trap with overflow arrangement, mixture fittings (with accessories), legs, grouting of legs etc with cement concrete all complete as required. | 27 | NOS | 1000 | 27000
14 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of shower tray with C.P. brass waste, C.I lugs and all other accessories | Receiving, shifting, installing and testing of shower tray with C.P. brass waste, C.I lugs and all other accessories, complete as required. | 166 | NOS | 500 | 83000
15 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of C.P. brass Bath tub mixture complete with all type of accessories | Receiving, shifting, installing and testing of C.P. brass Bath tub mixture complete with all type of accessories including Telephonic shower complete as required | 27 | NOS | 500 | 13500
16 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of C.P. brass mixer shower system & spout, wall flange | Receiving, shifting, installing and testing of C.P. brass mixer shower system & spout, wall flange, 190mm long heavy casted shower arm, wall flange and pressure adjustable Rain shower with all type of accessories complete as required. | 166 | NOS | 500 | 83000
17 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of stainless steel sink, (a) Single/double drain board supported by C.I./M.S. painted white brackets(b) C.P.cast brass bottle trap with extension piece(c) Rubber adapter(d) Wall flange (e) Union (f) C.P. brass chain rubber plug,Stainless steel sink as described above | Receiving, shifting, installing and testing of stainless steel sink with the following including cutting and making good the wall/floors complete as required.(a) Single/double drain board supported by C.I./M.S. painted white brackets(b) C.P.cast brass bottle trap with extension piece(c) Rubber adapter(d) Wall flange (e) Union (f) C.P. brass chain rubber plug,Stainless steel sink as described above | 12 | NOS | 800 | 9600
18 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of china Janitor sink, (a) CI/MS brackets(b) C.P. cast brass bottle trap with extension piece(c) Rubber adopter(d) Wall flange (e) Union(f) C.P. brass chain rubber plug,Janitor sink as described above | Receiving, shifting, installing and testing of viterous china Janitor sink with the following complete as required.(a) CI/MS brackets(b) C.P. cast brass bottle trap with extension piece(c) Rubber adopter(d) Wall flange (e) Union(f) C.P. brass chain rubber plug,Janitor sink as described above | 6 | NOS | 800 | 4800
19 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of C.P. brass sink mixer,(a) C.P.wall flange(b) Overhead swinging cast spout with areator Sink mixer as described above | Receiving, shifting, installing and testing of C.P. brass sink mixer with the following complete as required.(a) C.P.wall flange(b) Overhead swinging cast spout with areator Sink mixer as described above | 12 | NOS | 500 | 6000
20 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of C.P. brass sink cock with swing casted spout including C.P. brass wall flange. | Receiving, shifting, installing and testing of C.P. brass sink cock with swing casted spout including C.P. brass wall flange. | 6 | NOS | 400 | 2400
21 | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of fully hygienic hand drier of approved shade, (a)Double blower(b)Continous repeat usage(c)Time delay(d) Summer & winter control(e) Necessary brackets(f) Cable from drier to plug, plug to key & lock etc.Hand drier as described above | Receiving, shifting, installing and testing of solid state, no touch operating, fully hygienic hand drier of approved shade with the following complete as required.(a)Double blower(b)Continous repeat usage(c)Time delay(d) Summer & winter control(e) Necessary brackets(f) Cable from drier to plug, plug to key & lock etc.Hand drier as described above | 20 | NOS | 700 | 14000
a) | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of C.P. brass towel rail with C.P. brass wall brackets & C.P brass screws complete as required. | C.P. brass towel rail with C.P. brass wall brackets & C.P brass screws complete as required. | 166 | NOS | 100 | 16600
b) | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of Hand rail with T-piece and wall mounting for handicapped toilet | Hand rail with T-piece and wall mounting for handicapped toilet (Model RT 320 x 2 Nos. & RT 331 - 1 No.) | 4 | NOS | 100 | 400
c) | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of 35 mm dia powder coated steel grab bar (for handicapped toilet). | 35 mm dia powder coated steel grab bar (for handicapped toilet). | 4 | NOS | 100 | 400
d) | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of C.P. brass Towel ring | C.P. brass Towel ring | 12 | NOS | 100 | 1200
e) | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of C.P brass toilet paper holder. | C.P brass toilet paper holder. | 233 | NOS | 100 | 23300
f) | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of Toilet paper holder for handicapped toilet | Toilet paper holder for handicapped toilet | 4 | NOS | 100 | 400
g) | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of Recessed type S.S. soap dish with grab bar. | Recessed type S.S. soap dish with grab bar. | 27 | NOS | 100 | 2700
h) | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of Push button type liquid soap dispenser | Push button type liquid soap dispenser | 396 | NOS | 100 | 39600
i) | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of Paper dispenser | Paper dispenser | 20 | NOS | 100 | 2000
j) | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of C.P brass Bottle opener. | C.P brass Bottle opener. | 233 | NOS | 100 | 23300
k) | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of C.P. brass twin coat hook. | C.P. brass twin coat hook. | 233 | NOS | 100 | 23300
l) | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of Towel rack deluxe | Towel rack deluxe,Size 230 x 600 mm | 193 | NOS | 100 | 19300
m) | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of 15 mm dia C.P. brass bib cock (long body) & C.P. brass wall flange of approved quality. | 15 mm dia C.P. brass bib cock (long body) & C.P. brass wall flange of approved quality. | 20 | NOS | 100 | 2000
n) | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of 15 mm dia C.P. brass bib cock with Hose union & C.P. wall flange of approved quality | 15 mm dia C.P. brass bib cock with Hose union & C.P. wall flange of approved quality | 20 | NOS | 100 | 2000
o) | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of C.P. brass angle valve .(i) Filter(ii) C.P. brass flow regulator (flow 8 LPM)(iii) C.P. wall flange(iv) Nut and washer,Angle valve as described above | C.P. brass angle valve with the following complete as required.(i) Filter(ii) C.P. brass flow regulator (flow 8 LPM)(iii) C.P. wall flange(iv) Nut and washer,Angle valve as described above | 926 | NOS | 100 | 92600
p) | PLUMBING WORK | SANITARY FIXTURES, FITTINGS & ACCESSORIES |  | ITC of C.P Copper connection 375 mm | C.P Copper connection 375 mm long including nuts and washers and making connection to fixtures and fittings complete as required. | 926 | NOS | 100 | 92600
1(a) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe & Fittings SDR-11 15mm Dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 5600 | RM | 190 | 1064000
1(b) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe & Fittings SDR-11 20 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 2870 | RM | 220 | 631400
1( c ) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe & Fitting SDR-11 25 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 1170 | RM | 350 | 409500
1(d) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe & Fitting SDR-11 32 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 765 | RM | 400 | 306000
1( e ) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe & Fitting SDR-11 40 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 450 | RM | 500 | 225000
1(f) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe SDR-11 50 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 430 | RM | 700 | 301000
1(g) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe & Fitting SDR-11 65 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 1600 | RM | 2000 | 3200000
1(h) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe & Fitting SDR-11 80 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 535 | RM | 2600 | 1391000
1(i) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC PipeSDR-11 100 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 600 | RM | 4100 | 2460000
1( j ) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe & Fitting SDR-11 150 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 270 | RM | 8900 | 2403000
2(a) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe SDR-11, 15 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes for hot water system as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 6100 | RM | 190 | 1159000
2(b) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe & Fitting SDR-11 20 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes for hot water system as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 2650 | RM | 220 | 583000
2( c ) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe & Fitting SDR-11 25 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes for hot water system as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 1560 | RM | 350 | 546000
2(d) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe & Fitting SDR-11 32 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes for hot water system as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 560 | RM | 400 | 224000
2( e ) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe & Fitting SDR-11 40 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes for hot water system as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 680 | RM | 500 | 340000
2(f) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe & Fitting SDR-11 50 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes for hot water system as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 260 | RM | 700 | 182000
2(g) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe & Fitting SDR-11 65 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes for hot water system as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 320 | RM | 2000 | 640000
2(h) | PLUMBING WORK | WATER SUPPLY | CPVC SDR - 11 | SITC of CPVC Pipe & Fitting SDR-11 80 mm dia | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes for hot water system as per CTS SDR - 11 upto 2" dia and CPVC pipes shall confirm to ASTM F 441 schedule `80 Pipes and fitttings' above 2" dia at a working pressure of 28 kg/sqcm at 23 deg C and 7 kg/sqcm at 82 deg C, for jointing, using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings with galvanised angles, channels, clamp, hangers etc, as per specification. The item include cutting hole in wall, floor, slab and making 7.5 x 7.5 cm chasing in brick work with cutter for GI / Copper / MS / CPVC pipes and fittings & making good the same by using 1:1 cement mortar. | 450 | RM | 2600 | 1170000
3(a) | PLUMBING WORK | WATER SUPPLY | Concealed stop cock | SITC of extra heavy duty C.P. brass concealed stop cock, 15 mm dia | Providing and fixing extra heavy duty C.P. brass concealed stop cock with adjustable wall flange | 20 | NOS | 1000 | 20000
3(b) | PLUMBING WORK | WATER SUPPLY | Concealed stop cock | SITC of extra heavy duty C.P. brass concealed stop cock, 20 mm dia | Providing and fixing extra heavy duty C.P. brass concealed stop cock with adjustable wall flange | 20 | NOS | 1200 | 24000
4(a) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of brass ball valve 15 mm dia, PN-10 | Providing & fixing lever operated brass ball valve with stainless steel ball / stem. for working pressure of 10 Kg / Sqcm for domestic and hot water supply. Including flanges/union, nuts, bolts, washer etc. complete as required. | 430 | NOS | 550 | 236500
4(b) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of brass ball valve 20 mm dia, PN-10 | Providing & fixing lever operated brass ball valve with stainless steel ball / stem. for working pressure of 10 Kg / Sqcm for domestic and hot water supply. Including flanges/union, nuts, bolts, washer etc. complete as required. | 505 | NOS | 700 | 353500
4( c ) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of brass ball valve 25 mm dia, PN-10 | Providing & fixing lever operated brass ball valve with stainless steel ball / stem. for working pressure of 10 Kg / Sqcm for domestic and hot water supply. Including flanges/union, nuts, bolts, washer etc. complete as required. | 60 | NOS | 1302 | 78120
4(d) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of brass ball valve 32 mm dia, PN-10 | Providing & fixing lever operated brass ball valve with stainless steel ball / stem. for working pressure of 10 Kg / Sqcm for domestic and hot water supply. Including flanges/union, nuts, bolts, washer etc. complete as required. | 30 | NOS | 2100 | 63000
4( e ) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of brass ball valve 40 mm dia, PN-10 | Providing & fixing lever operated brass ball valve with stainless steel ball / stem. for working pressure of 10 Kg / Sqcm for domestic and hot water supply. Including flanges/union, nuts, bolts, washer etc. complete as required. | 55 | NOS | 3000 | 165000
4(f) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of brass ball valve 50 mm dia, PN-10 | Providing & fixing lever operated brass ball valve with stainless steel ball / stem. for working pressure of 10 Kg / Sqcm for domestic and hot water supply. Including flanges/union, nuts, bolts, washer etc. complete as required. | 35 | NOS | 4900 | 171500
4(g) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of brass ball valve 65 mm dia, PN-10 | Providing & fixing lever operated brass ball valve with stainless steel ball / stem. for working pressure of 10 Kg / Sqcm for domestic and hot water supply. Including flanges/union, nuts, bolts, washer etc. complete as required. | 95 | NOS | 8000 | 760000
5(a) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of butterfly valve 80 mm dia, PN-10 | Providing & fixing CI butterfly valve with hand lever operation & above with gear box operation). suitable for working pressure of 10 Kg / Sqcm.Including rubber gasket, flanges, nuts, bolts, washers & painting complete as required. | 25 | NOS | 4000 | 100000
5(b) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of butterfly valve 100 mm dia, PN-10 | Providing & fixing CI butterfly valve with hand lever operation & above with gear box operation). suitable for working pressure of 10 Kg / Sqcm.Including rubber gasket, flanges, nuts, bolts, washers & painting complete as required. | 40 | NOS | 5100 | 204000
5( c ) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of butterfly valve 150 mm dia, PN-10 | Providing & fixing CI butterfly valve with hand lever operation & above with gear box operation). suitable for working pressure of 10 Kg / Sqcm.Including rubber gasket, flanges, nuts, bolts, washers & painting complete as required. | 25 | NOS | 8500 | 212500
6(a) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of non return valve 65 mm dia, PN-10 | Providing & fixing gun metal horizontal flap type non return valve conforming to IS 778 and suitable for working pressure of 10 Kg / Sqcm. Including rubber gasket, flanges, union, nuts, bolts & washers complete as required. | 30 | NOS | 6000 | 180000
7(a) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of C.I. wafer type check valve 80 mm dia, PN-10 | Providing & fixing C.I. wafer type check valve suitable for working pressure of 10 Kg / Sqcm. Including rubber gasket, flanges, union, nuts, bolts, washers & painting complete as required. | 2 | NOS | 7500 | 15000
7(b) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of C.I. wafer type check valve 100 mm dia, PN-10 | Providing & fixing C.I. wafer type check valve suitable for working pressure of 10 Kg / Sqcm. Including rubber gasket, flanges, union, nuts, bolts, washers & painting complete as required. | 8 | NOS | 8700 | 69600
8(a) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of solenoid valve 40 mm dia, PN-10 | Providing & fixing gun metal two way solenoid valve conforming to IS 778 and suitable for working pressure of 10 Kg / Sqcm. Including rubber gasket, flanges, union, nuts, bolts & washers complete as required. | 1 | NOS | 5600 | 5600
8(b) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of solenoid valve 65 mm dia, PN-10 | Providing & fixing gun metal two way solenoid valve conforming to IS 778 and suitable for working pressure of 10 Kg / Sqcm. Including rubber gasket, flanges, union, nuts, bolts & washers complete as required. | 3 | NOS | 5900 | 17700
9(a) | PLUMBING WORK | WATER SUPPLY | Rubber Expansion | SITC of twin sphere connectors, with union treads rubber expansion joint , 100 mm dia, PN-10 | Providing and fixing twin sphere connectors with union treads rubber expansion joint with unit control as per manufacturers specifications of standard length complete with all accessories suitable for working pressure of 10 Kg / Sqcm. Including rubber gaskets, flanges, nuts, bolts & washers complete as required.Suitable for cold & hws system. | 6 | NOS | 9950 | 59700
9(b) | PLUMBING WORK | WATER SUPPLY | Rubber Expansion | SITC of twin sphere connectors, with union treads rubber expansion joint,150 mm dia, PN-10 | Providing and fixing twin sphere connectors with union treads rubber expansion joint with unit control as per manufacturers specifications of standard length complete with all accessories suitable for working pressure of 10 Kg / Sqcm. Including rubber gaskets, flanges, nuts, bolts & washers complete as required.Suitable for cold & hws system. | 6 | NOS | 12390 | 74340
10(a) | PLUMBING WORK | WATER SUPPLY | `Y' Strainer | SITC of `Y' Strainer, 150 mm dia | Providing & fixing `Y' Strainer (screwed/ flanged)with cleaning arrangement and stainless steel fine wire mesh perforated sheet basket with necessary flange/ unions nuts, bolts and washers complete as required. | 6 | NOS | 15000 | 90000
11(a) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of G.M. float valve with copper ball, 25 mm dia, PN-10 | Providing and fixing of approved quality G.M. float valve with copper ball float and brass rods of required length suitable for test pressure of 10 Kg/sqcm of the required sizes | 5 | NO | 3400 | 17000
11(b) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of G.M. float valve with copper ball, 40 mm dia, PN-10 | Providing and fixing of approved quality G.M. float valve with copper ball float and brass rods of required length suitable for test pressure of 10 Kg/sqcm of the required sizes | 1 | NO | 4500 | 4500
11( c ) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of G.M. float valve with copper ball, 65 mm dia, PN-10 | Providing and fixing of approved quality G.M. float valve with copper ball float and brass rods of required length suitable for test pressure of 10 Kg/sqcm of the required sizes | 3 | NO | 7900 | 23700
12(a) | PLUMBING WORK | WATER SUPPLY | flow meter | SITC of flow meter, 15 mm dia | Providing & fixing on line digital type flow meter with preamplifier & microprocessor based electronic flow meter mounted in plumbing plant room electrical control panel with the following features. Monitoring the total flow, Flow rate, high low arm batching and blending etc. Including electrical wiring from preamplifier to microprocessor based flow meter. Complete with all type of Plumbing & Electricla connections, accessories, wiring, conduits & supports complete with all respect. The signal read out shall be 4-20 m.amps to be received as BAS.(PTSE). Flow meter should be compatible to BMS system. | 10 | NOS | 2500 | 25000
12(b) | PLUMBING WORK | WATER SUPPLY | flow meter | SITC of flow meter, 20 mm dia | Providing & fixing on line digital type flow meter with preamplifier & microprocessor based electronic flow meter mounted in plumbing plant room electrical control panel with the following features. Monitoring the total flow, Flow rate, high low arm batching and blending etc. Including electrical wiring from preamplifier to microprocessor based flow meter. Complete with all type of Plumbing & Electricla connections, accessories, wiring, conduits & supports complete with all respect. The signal read out shall be 4-20 m.amps to be received as BAS.(PTSE). Flow meter should be compatible to BMS system. | 5 | NOS | 3900 | 19500
12( c ) | PLUMBING WORK | WATER SUPPLY | flow meter | SITC of flow meter, 25 mm dia | Providing & fixing on line digital type flow meter with preamplifier & microprocessor based electronic flow meter mounted in plumbing plant room electrical control panel with the following features. Monitoring the total flow, Flow rate, high low arm batching and blending etc. Including electrical wiring from preamplifier to microprocessor based flow meter. Complete with all type of Plumbing & Electricla connections, accessories, wiring, conduits & supports complete with all respect. The signal read out shall be 4-20 m.amps to be received as BAS.(PTSE). Flow meter should be compatible to BMS system. | 5 | NOS | 4200 | 21000
12(d) | PLUMBING WORK | WATER SUPPLY | flow meter | SITC of flow meter, 32 mm dia | Providing & fixing on line digital type flow meter with preamplifier & microprocessor based electronic flow meter mounted in plumbing plant room electrical control panel with the following features. Monitoring the total flow, Flow rate, high low arm batching and blending etc. Including electrical wiring from preamplifier to microprocessor based flow meter. Complete with all type of Plumbing & Electricla connections, accessories, wiring, conduits & supports complete with all respect. The signal read out shall be 4-20 m.amps to be received as BAS.(PTSE). Flow meter should be compatible to BMS system. | 6 | NOS | 5000 | 30000
12( e ) | PLUMBING WORK | WATER SUPPLY | flow meter | SITC of flow meter, 40 mm dia | Providing & fixing on line digital type flow meter with preamplifier & microprocessor based electronic flow meter mounted in plumbing plant room electrical control panel with the following features. Monitoring the total flow, Flow rate, high low arm batching and blending etc. Including electrical wiring from preamplifier to microprocessor based flow meter. Complete with all type of Plumbing & Electricla connections, accessories, wiring, conduits & supports complete with all respect. The signal read out shall be 4-20 m.amps to be received as BAS.(PTSE). Flow meter should be compatible to BMS system. | 10 | NOS | 6000 | 60000
12(f) | PLUMBING WORK | WATER SUPPLY | flow meter | SITC of flow meter, 50 mm dia | Providing & fixing on line digital type flow meter with preamplifier & microprocessor based electronic flow meter mounted in plumbing plant room electrical control panel with the following features. Monitoring the total flow, Flow rate, high low arm batching and blending etc. Including electrical wiring from preamplifier to microprocessor based flow meter. Complete with all type of Plumbing & Electricla connections, accessories, wiring, conduits & supports complete with all respect. The signal read out shall be 4-20 m.amps to be received as BAS.(PTSE). Flow meter should be compatible to BMS system. | 10 | NOS | 7000 | 70000
12(g) | PLUMBING WORK | WATER SUPPLY | flow meter | SITC of flow meter, 65 mm dia | Providing & fixing on line digital type flow meter with preamplifier & microprocessor based electronic flow meter mounted in plumbing plant room electrical control panel with the following features. Monitoring the total flow, Flow rate, high low arm batching and blending etc. Including electrical wiring from preamplifier to microprocessor based flow meter. Complete with all type of Plumbing & Electricla connections, accessories, wiring, conduits & supports complete with all respect. The signal read out shall be 4-20 m.amps to be received as BAS.(PTSE). Flow meter should be compatible to BMS system. | 6 | NOS | 11000 | 66000
12(h) | PLUMBING WORK | WATER SUPPLY | flow meter | SITC of flow meter, 80 mm dia | Providing & fixing on line digital type flow meter with preamplifier & microprocessor based electronic flow meter mounted in plumbing plant room electrical control panel with the following features. Monitoring the total flow, Flow rate, high low arm batching and blending etc. Including electrical wiring from preamplifier to microprocessor based flow meter. Complete with all type of Plumbing & Electricla connections, accessories, wiring, conduits & supports complete with all respect. The signal read out shall be 4-20 m.amps to be received as BAS.(PTSE). Flow meter should be compatible to BMS system. | 8 | NOS | 15000 | 120000
12(i) | PLUMBING WORK | WATER SUPPLY | flow meter | SITC of flow meter, 100 mm dia | Providing & fixing on line digital type flow meter with preamplifier & microprocessor based electronic flow meter mounted in plumbing plant room electrical control panel with the following features. Monitoring the total flow, Flow rate, high low arm batching and blending etc. Including electrical wiring from preamplifier to microprocessor based flow meter. Complete with all type of Plumbing & Electricla connections, accessories, wiring, conduits & supports complete with all respect. The signal read out shall be 4-20 m.amps to be received as BAS.(PTSE). Flow meter should be compatible to BMS system. | 10 | NOS | 16000 | 160000
13(a) | PLUMBING WORK | WATER SUPPLY |  | SITC of, Making cold / hot water supply connection to kitchen / laundary equipments, (pipes and valves to be paid separately).15 mm dia to 25 mm dia | Making cold / hot water supply connection to kitchen / laundary equipments, appliances, coolers etc. including necessary fittings, (pipes and valves to be paid separately). | 80 | NOS | 1500 | 120000
14(a) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of, Auto Air vent with ball valve, 15 mm dia, PN-10 | Providing & fixing Auto Air vent with ball valve for cold / hot water supply risers, suitable for working pressure of 10 Kg/Sq.cm. | 140 | NOS | 2500 | 350000
15(a) | PLUMBING WORK | WATER SUPPLY | Rubber Insulation | SITC of, nitrile rubber insulation for exposed, 15 mm dia pipe --- SP insulation 9 mm thick | Supply, installing and testing of nitrile rubber insulation for exposed & concealed hot water supply pipes and fittings, strainer and valves etc. | 6100 | RM | 40 | 244000
15(b) | PLUMBING WORK | WATER SUPPLY | Rubber Insulation | SITC of, nitrile rubber insulation for exposed, 20 mm dia pipe --- SP insulation 9 mm thick | Supply, installing and testing of nitrile rubber insulation for exposed & concealed hot water supply pipes and fittings, strainer and valves etc. | 2650 | RM | 60 | 159000
15( c ) | PLUMBING WORK | WATER SUPPLY | Rubber Insulation | SITC of, nitrile rubber insulation for exposed | Supply, installing and testing of nitrile rubber insulation for exposed & concealed hot water supply pipes and fittings, strainer and valves etc. | 1560 | RM | 70 | 109200
15(d) | PLUMBING WORK | WATER SUPPLY | Rubber Insulation | SITC of, nitrile rubber insulation for exposed, 25 mm dia pipe --- SP insulation 9 mm thick | Supply, installing and testing of nitrile rubber insulation for exposed & concealed hot water supply pipes and fittings, strainer and valves etc. | 560 | RM | 90 | 50400
15( e ) | PLUMBING WORK | WATER SUPPLY | Rubber Insulation | SITC of, nitrile rubber insulation for exposed, 40 mm dia pipe --- SP insulation 13 mm thick | Supply, installing and testing of nitrile rubber insulation for exposed & concealed hot water supply pipes and fittings, strainer and valves etc. | 680 | RM | 100 | 68000
15(f) | PLUMBING WORK | WATER SUPPLY | Rubber Insulation | SITC of, nitrile rubber insulation for exposed, 50 mm dia pipe --- SP insulation 19 mm thick | Supply, installing and testing of nitrile rubber insulation for exposed & concealed hot water supply pipes and fittings, strainer and valves etc. | 260 | RM | 120 | 31200
15(g) | PLUMBING WORK | WATER SUPPLY | Rubber Insulation | SITC of, nitrile rubber insulation for exposed, 65 mm dia pipe --- SP insulation 25 mm thick | Supply, installing and testing of nitrile rubber insulation for exposed & concealed hot water supply pipes and fittings, strainer and valves etc. | 320 | RM | 180 | 57600
15(h) | PLUMBING WORK | WATER SUPPLY | Rubber Insulation | SITC of, nitrile rubber insulation for exposed, 80 mm dia pipe --- SP insulation 25 mm thick | Supply, installing and testing of nitrile rubber insulation for exposed & concealed hot water supply pipes and fittings, strainer and valves etc. | 450 | RM | 190 | 85500
16(a) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of CI butterfly valve, 80 mm dia, PN-10 | Providing & fixing CI butterfly valve with hand lever operation & above with gear box operation). suitable for working pressure of 10 Kg / Sqcm.Including rubber gasket, flanges, nuts, bolts, washers & painting complete as required for hot water system and insulation as per item no. 24. | 10 | NOS | 6900 | 69000
17(a) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of , gun metal globe valve with CI hand wheel union flanges, 15 mm dia, PN-15 | Providing & fixing gun metal globe valve with CI hand wheel union flanges,washer nuts & bolts rated to a temperature of 85 Deg C & suitable for pressure 15 kg/sqcm with LRB machine stiched matteresses insulation 50 mm thick of density 150kg / cum backed with hexagonical wire netting on one side. And tying with GI wire to hold the matteresses. | 250 | NOS | 900 | 225000
17(b) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of , gun metal globe valve with CI hand wheel union flanges, 20 mm dia, PN-15 | Providing & fixing gun metal globe valve with CI hand wheel union flanges,washer nuts & bolts rated to a temperature of 85 Deg C & suitable for pressure 15 kg/sqcm with LRB machine stiched matteresses insulation 50 mm thick of density 150kg / cum backed with hexagonical wire netting on one side. And tying with GI wire to hold the matteresses. | 40 | NOS | 1000 | 40000
17( c ) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of , gun metal globe valve with CI hand wheel union flanges, 25 mm dia, PN-15 | Providing & fixing gun metal globe valve with CI hand wheel union flanges,washer nuts & bolts rated to a temperature of 85 Deg C & suitable for pressure 15 kg/sqcm with LRB machine stiched matteresses insulation 50 mm thick of density 150kg / cum backed with hexagonical wire netting on one side. And tying with GI wire to hold the matteresses. | 30 | NOS | 1200 | 36000
17(d) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of , gun metal globe valve with CI hand wheel union flanges, 32 mm dia, PN-15 | Providing & fixing gun metal globe valve with CI hand wheel union flanges,washer nuts & bolts rated to a temperature of 85 Deg C & suitable for pressure 15 kg/sqcm with LRB machine stiched matteresses insulation 50 mm thick of density 150kg / cum backed with hexagonical wire netting on one side. And tying with GI wire to hold the matteresses. | 5 | NOS | 2900 | 14500
17( e ) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of , gun metal globe valve with CI hand wheel union flanges, 40 mm dia, PN-15 | Providing & fixing gun metal globe valve with CI hand wheel union flanges,washer nuts & bolts rated to a temperature of 85 Deg C & suitable for pressure 15 kg/sqcm with LRB machine stiched matteresses insulation 50 mm thick of density 150kg / cum backed with hexagonical wire netting on one side. And tying with GI wire to hold the matteresses. | 10 | NOS | 3900 | 39000
17(f) | PLUMBING WORK | WATER SUPPLY | Valve | SITC of , gun metal globe valve with CI hand wheel union flanges, 65 mm dia, PN-15 | Providing & fixing gun metal globe valve with CI hand wheel union flanges,washer nuts & bolts rated to a temperature of 85 Deg C & suitable for pressure 15 kg/sqcm with LRB machine stiched matteresses insulation 50 mm thick of density 150kg / cum backed with hexagonical wire netting on one side. And tying with GI wire to hold the matteresses. | 4 | NOS | 12000 | 48000
18(a) | PLUMBING WORK | WATER SUPPLY | nitrile rubber insulation | SITC of nitrile rubber insulation, 15 mm dia to 40 mm dia pipe | Providing and fixing 22 SWG Al. sheet cladding over nitrile rubber insulation on hot water pipe work including valves and fittings for the following size pipes. | 2500 | RM | 130 | 325000
18(b) | PLUMBING WORK | WATER SUPPLY | nitrile rubber insulation | SITC of nitrile rubber insulation, 50 mm dia to 80 mm dia pipe | Providing and fixing 22 SWG Al. sheet cladding over nitrile rubber insulation on hot water pipe work including valves and fittings for the following size pipes. | 1030 | RM | 200 | 206000
19(a) | PLUMBING WORK | WATER SUPPLY |  | SITC of gun metal /brass, 65 mm dia | Providing and fixing water meter with direct reading dial in KL with all integral parts of gun metal /brass with neccesary fittings such as threaded pieces, unions pressure guage and isolation cock, flanges piece for future removal, flanges/unions complete with all necessary testing charges and obtaining test cetificates from local municipal authorities. | 1 | NOS | 13000 | 13000
20(a) | PLUMBING WORK | WATER SUPPLY | U-PVC Sch 80 | SITC of U-PVC Sch 80 Pipe & Fitting, 25 mm dia | Providing, fixing, jointing and testing in position the following U-PVC Sch 80 pressure pipes as per ASTM D 1785 with threaded / solvent cement joint fitting, including all necessary fittings and specials such as bends, tees, union, reducers, flanges and plugs etc. The pipes and fittings shall be suitable of working pressure of 10 Kg/Sq.cm and making good the same complete as required (All pipes sizes shall be considered as internal dia of pipe and pipe shall be used for external water supply services) | 90 | RM | 400 | 36000
20(b) | PLUMBING WORK | WATER SUPPLY | U-PVC Sch 80 | SITC of U-PVC Sch 80 pipes as per ASTM D 1785, 40 mm dia | Providing, fixing, jointing and testing in position the following U-PVC Sch 80 pressure pipes as per ASTM D 1785 with threaded / solvent cement joint fitting, including all necessary fittings and specials such as bends, tees, union, reducers, flanges and plugs etc. The pipes and fittings shall be suitable of working pressure of 10 Kg/Sq.cm and making good the same complete as required (All pipes sizes shall be considered as internal dia of pipe and pipe shall be used for external water supply services) | 30 | RM | 590 | 17700
20( c ) | PLUMBING WORK | WATER SUPPLY | U-PVC Sch 80 | SITC of U-PVC Sch 80 pipes as per ASTM D 1785, 65 mm dia | Providing, fixing, jointing and testing in position the following U-PVC Sch 80 pressure pipes as per ASTM D 1785 with threaded / solvent cement joint fitting, including all necessary fittings and specials such as bends, tees, union, reducers, flanges and plugs etc. The pipes and fittings shall be suitable of working pressure of 10 Kg/Sq.cm and making good the same complete as required (All pipes sizes shall be considered as internal dia of pipe and pipe shall be used for external water supply services) | 40 | RM | 860 | 34400
20(d) | PLUMBING WORK | WATER SUPPLY | U-PVC Sch 80 | SITC of U-PVC Sch 80 pipes as per ASTM D 1785, 100 mm dia | Providing, fixing, jointing and testing in position the following U-PVC Sch 80 pressure pipes as per ASTM D 1785 with threaded / solvent cement joint fitting, including all necessary fittings and specials such as bends, tees, union, reducers, flanges and plugs etc. The pipes and fittings shall be suitable of working pressure of 10 Kg/Sq.cm and making good the same complete as required (All pipes sizes shall be considered as internal dia of pipe and pipe shall be used for external water supply services) | 520 | RM | 1200 | 624000
21(a) | PLUMBING WORK | WATER SUPPLY |  | SITC of , GI/CU/CILA/PVC pipes, Pipe Upto 150 mm dia | Providing trenching upto required depth but not less than 1 mt. deep for embedded GI/CU/CILA/PVC pipes and fittings. Providing 100 mm thick fine sand filling all round the pipe. inlcuding excavation in all kind of soil (hard rock), dewatering refilling, watering, ramming and removing the surplus excavated material and making good the same as per Architect requirement. | 350 | RM | 150 | 52500
23 | PLUMBING WORK | WATER SUPPLY |  | SITC of 25 mm dia lawn hydrants consisting of 25 mm dia Ball valve G.I. nipple and threaded hose receiver | Providing and fixing 25 mm dia lawn hydrants consisting of 25 mm dia Ball valve G.I. nipple and threaded hose receiver complete as required. | 20 | NOS | 900 | 18000
24(a) | PLUMBING WORK | WATER SUPPLY | Chamber | Constructing brick masonary chamber, Size 450 x 450 x 600 mm deep | Constructing brick masonary chamber (for housing valves, Meters etc.) of brick work with of class desgination 75 in cement mortar 1 : 5 (1 cement:5 finesand) plastering internal face with cement mortar 1 : 3 (1 cement: 3 fine sand and rough plaster on outer face with floating coat of neat cement. 150mm thick PCC in 1:4:8, R.C.C top slab for fixing the manhole cover with frame. Including excavation in all kind of soil dewatering, refilling, watering, ramming and shifting of surplus excavated material by contractor within the site limit as directed by the the site incharge and making good the same complete as required. | 20 | NOS | 6000 | 120000
24(b) | PLUMBING WORK | WATER SUPPLY | Chamber | Constructing brick masonary chamber, Size 600 x 600 x 750 mm deep | Constructing brick masonary chamber (for housing valves, Meters etc.) of brick work with of class desgination 75 in cement mortar 1 : 5 (1 cement:5 finesand) plastering internal face with cement mortar 1 : 3 (1 cement: 3 fine sand and rough plaster on outer face with floating coat of neat cement. 150mm thick PCC in 1:4:8, R.C.C top slab for fixing the manhole cover with frame. Including excavation in all kind of soil dewatering, refilling, watering, ramming and shifting of surplus excavated material by contractor within the site limit as directed by the the site incharge and making good the same complete as required. | 3 | NOS | 9000 | 27000
24( c ) | PLUMBING WORK | WATER SUPPLY | Chamber | Constructing brick masonary chamber, Size 1000 x 800 x 1200 mm deep | Constructing brick masonary chamber (for housing valves, Meters etc.) of brick work with of class desgination 75 in cement mortar 1 : 5 (1 cement:5 finesand) plastering internal face with cement mortar 1 : 3 (1 cement: 3 fine sand and rough plaster on outer face with floating coat of neat cement. 150mm thick PCC in 1:4:8, R.C.C top slab for fixing the manhole cover with frame. Including excavation in all kind of soil dewatering, refilling, watering, ramming and shifting of surplus excavated material by contractor within the site limit as directed by the the site incharge and making good the same complete as required. | 1 | NOS | 12000 | 12000
25(a) | PLUMBING WORK | WATER SUPPLY | Chamber Cover | SITC of heavy duty manhole cover, Size 450mm x 450mm(MD) | Providing and fixing hinges type heavy duty manhole cover with frame of the following sizes: | 20 | NOS | 3500 | 70000
25(b) | PLUMBING WORK | WATER SUPPLY | Chamber Cover | SITC of heavy duty manhole cover, Size 600mm x 600mm(HD wt. 90 kg) | Providing and fixing hinges type heavy duty manhole cover with frame of the following sizes: | 4 | NOS | 3800 | 15200
1(a) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | PP LN Pipe | SITC of Polypropylene low noise pipes & Fitting 75 mm dia | Providing, fixing, jointing, testinSupply, installation, testing & commissioning of mineral filled multilayer (PP/PP mineral filled/PP) Polypropylene low noise pipes confirming to EN 1451 including all fittings & accessories such as coupler, elbow, tee, Y, reducer, access door, end cap, cowls, clamps, etc. for conveying soil, waste, vent & rainwater purpose in floors, ceiling suspended, or on walls, with leak proof joints etc. Joining pipes & fittings with SBR rubber sealing rings as per approved manufacturer recommendation Sound level of less than or equal to 4 db(A) at flow rate of 4 Lis according to EN 14366. Material density should not be less than 1.9 gm/cm3 Modulus of elasticity 3800 N/mm2 & ring stiffness 21KN/m2. Tensile strength 16.8 N/mm2 & coef. of linear expansion 0.09 Mm/mk. MFR 2.1 gm/10 min Fire resistance of D-s2, d0 as per EN 13501- 1 & DIN 4102:B2 Joining method - Push fit sockets with factory inserted lip seal. Testing as per tender specifications/ElC. Make Astral/PoIopIast/Rehau and commissioning spun/centri C.I. pipe for soil, waste, vent and rain water pipes installation conforming to IS:3989 cut to required lengths including all necessary fittings and specials such as Bends, junctions, offsets, access pieces (plain or door) & vent cowl. Fixing at wall/ceiling level supported by GI angle, chanel, clamps & hangers etc. Making connection with drip seal joint of required depth as per manufacturer. Cutting, chases/holes in floors / walls / slab and And G.I. Heavy class pipe sleeve of one size larger diameter shall be provided wherever the pipes are crossing the fire rated walls / floors ,slab and sealing the sleeves with glass wool in between and fire sealent compound at either ends. The item include cutting hole in wall, floor,slab and making good the same with required material. (Including painting as per item no 24 & making trenches as per item no 2). | 925 | RM | 820 | 758500
1(b) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | PP LN Pipe | SITC of Polypropylene low noise pipes & Fitting 100 mm dia | Providing, fixing, jointing, testinSupply, installation, testing & commissioning of mineral filled multilayer (PP/PP mineral filled/PP) Polypropylene low noise pipes confirming to EN 1451 including all fittings & accessories such as coupler, elbow, tee, Y, reducer, access door, end cap, cowls, clamps, etc. for conveying soil, waste, vent & rainwater purpose in floors, ceiling suspended, or on walls, with leak proof joints etc. Joining pipes & fittings with SBR rubber sealing rings as per approved manufacturer recommendation Sound level of less than or equal to 4 db(A) at flow rate of 4 Lis according to EN 14366. Material density should not be less than 1.9 gm/cm3 Modulus of elasticity 3800 N/mm2 & ring stiffness 21KN/m2. Tensile strength 16.8 N/mm2 & coef. of linear expansion 0.09 Mm/mk. MFR 2.1 gm/10 min Fire resistance of D-s2, d0 as per EN 13501- 1 & DIN 4102:B2 Joining method - Push fit sockets with factory inserted lip seal. Testing as per tender specifications/ElC. Make Astral/PoIopIast/Rehau and commissioning spun/centri C.I. pipe for soil, waste, vent and rain water pipes installation conforming to IS:3989 cut to required lengths including all necessary fittings and specials such as Bends, junctions, offsets, access pieces (plain or door) & vent cowl. Fixing at wall/ceiling level supported by GI angle, chanel, clamps & hangers etc. Making connection with drip seal joint of required depth as per manufacturer. Cutting, chases/holes in floors / walls / slab and And G.I. Heavy class pipe sleeve of one size larger diameter shall be provided wherever the pipes are crossing the fire rated walls / floors ,slab and sealing the sleeves with glass wool in between and fire sealent compound at either ends. The item include cutting hole in wall, floor,slab and making good the same with required material. (Including painting as per item no 24 & making trenches as per item no 2). | 5300 | RM | 1366 | 7239800
1( c ) | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | PP LN Pipe | SITC of SITC of Polypropylene low noise pipes & Fitting 150 mm dia | Providing, fixing, jointing, testinSupply, installation, testing & commissioning of mineral filled multilayer (PP/PP mineral filled/PP) Polypropylene low noise pipes confirming to EN 1451 including all fittings & accessories such as coupler, elbow, tee, Y, reducer, access door, end cap, cowls, clamps, etc. for conveying soil, waste, vent & rainwater purpose in floors, ceiling suspended, or on walls, with leak proof joints etc. Joining pipes & fittings with SBR rubber sealing rings as per approved manufacturer recommendation Sound level of less than or equal to 4 db(A) at flow rate of 4 Lis according to EN 14366. Material density should not be less than 1.9 gm/cm3 Modulus of elasticity 3800 N/mm2 & ring stiffness 21KN/m2. Tensile strength 16.8 N/mm2 & coef. of linear expansion 0.09 Mm/mk. MFR 2.1 gm/10 min Fire resistance of D-s2, d0 as per EN 13501- 1 & DIN 4102:B2 Joining method - Push fit sockets with factory inserted lip seal. Testing as per tender specifications/ElC. Make Astral/PoIopIast/Rehau and commissioning spun/centri C.I. pipe for soil, waste, vent and rain water pipes installation conforming to IS:3989 cut to required lengths including all necessary fittings and specials such as Bends, junctions, offsets, access pieces (plain or door) & vent cowl. Fixing at wall/ceiling level supported by GI angle, chanel, clamps & hangers etc. Making connection with drip seal joint of required depth as per manufacturer. Cutting, chases/holes in floors / walls / slab and And G.I. Heavy class pipe sleeve of one size larger diameter shall be provided wherever the pipes are crossing the fire rated walls / floors ,slab and sealing the sleeves with glass wool in between and fire sealent compound at either ends. The item include cutting hole in wall, floor,slab and making good the same with required material. (Including painting as per item no 24 & making trenches as per item no 2). | 2650 | RM | 2052 | 5437800
1(d) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | PP LN Pipe | SITC of C.I. Pipe & Fitting 200 mm dia | Providing, fixing, jointing, testinSupply, installation, testing & commissioning of mineral filled multilayer (PP/PP mineral filled/PP) Polypropylene low noise pipes confirming to EN 1451 including all fittings & accessories such as coupler, elbow, tee, Y, reducer, access door, end cap, cowls, clamps, etc. for conveying soil, waste, vent & rainwater purpose in floors, ceiling suspended, or on walls, with leak proof joints etc. Joining pipes & fittings with SBR rubber sealing rings as per approved manufacturer recommendation Sound level of less than or equal to 4 db(A) at flow rate of 4 Lis according to EN 14366. Material density should not be less than 1.9 gm/cm3 Modulus of elasticity 3800 N/mm2 & ring stiffness 21KN/m2. Tensile strength 16.8 N/mm2 & coef. of linear expansion 0.09 Mm/mk. MFR 2.1 gm/10 min Fire resistance of D-s2, d0 as per EN 13501- 1 & DIN 4102:B2 Joining method - Push fit sockets with factory inserted lip seal. Testing as per tender specifications/ElC. Make Astral/PoIopIast/Rehau and commissioning spun/centri C.I. pipe for soil, waste, vent and rain water pipes installation conforming to IS:3989 cut to required lengths including all necessary fittings and specials such as Bends, junctions, offsets, access pieces (plain or door) & vent cowl. Fixing at wall/ceiling level supported by GI angle, chanel, clamps & hangers etc. Making connection with drip seal joint of required depth as per manufacturer. Cutting, chases/holes in floors / walls / slab and And G.I. Heavy class pipe sleeve of one size larger diameter shall be provided wherever the pipes are crossing the fire rated walls / floors ,slab and sealing the sleeves with glass wool in between and fire sealent compound at either ends. The item include cutting hole in wall, floor,slab and making good the same with required material. (Including painting as per item no 24 & making trenches as per item no 2). | 255 | RM | 3000 | 765000
2(a) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | C.I. pipe | SITC of C.I. Pipe & Fitting 200 mm dia | Same as item no. 1 but pipes are running below ground in trenches upto 1st manhole depth as required ,including excavation in all kind of soil, refilling, watering, ramming and removing the surpluses excavated material and making good the same. | 50 | RM | 5200 | 260000
3(a) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | Civil | SITC of C.I. / C.I. class L.A. pipes, For 75 mm dia pipe, 100mm thick alround and 100 thick bed concrete | Providing and laying 1:2:4 cement conc. all round the pipe including bed concrete for the following C.I. / C.I. class L.A. pipes and specials below floor including necessary shuttering etc. complete as required and steel reinforcement if required. | 220 | RM | 200 | 44000
3(b) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | Civil | SITC of C.I. / C.I. class L.A. pipes, For 100 mm dia pipe, 100mm thick alround and 100 thick bed concrete | Providing and laying 1:2:4 cement conc. all round the pipe including bed concrete for the following C.I. / C.I. class L.A. pipes and specials below floor including necessary shuttering etc. complete as required and steel reinforcement if required. | 650 | RM | 210 | 136500
3( c ) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | Civil | SITC of C.I. / C.I. class L.A. pipes, For 150 mm dia pipe, 150mm thick alround and 150 thick bed concrete | Providing and laying 1:2:4 cement conc. all round the pipe including bed concrete for the following C.I. / C.I. class L.A. pipes and specials below floor including necessary shuttering etc. complete as required and steel reinforcement if required. | 400 | RM | 300 | 120000
4(a) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | Traps | SITC of CI full bore "P"/ "S" trap (IS:3989), 100 mm inlet and 100 mm outlet. | Providing & fixing in position CI full bore "P"/ "S" trap (IS:3989). Making proper connection with drip seal. Cutting chase / hole in floors /slabs and making good the same after placing the trap complete as required. The trap shall have minimum 50mm deep water seal and shall be supported by GI clamps hanger as per Consultant. | 600 | NOS | 900 | 540000
5 | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | FD | SITC of reducing elbow 110mm x 63mm dia waste (for shower) | Providing and fixing 110mm x 63mm dia waste (for shower) made from 110mm x63mm reducing elbow with heavy class extension piece upto grating, including cutting chases, the floor / slab complete as required and making connection to waste pipe. | 325 | NOS | 600 | 195000
6 | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | Hopper | SITC of heavy class PVC inlet hopper with required inlets | Providing and fixing heavy class PVC inlet hopper with required inlets fittings (connection to be done with saddle) to receive waste from fixtures waste. The hopper shall be fabricated from 110 mm dia upto 750 mm long PVC pipe with PVC socket or required fitting suitable for connection to the waste. Support by galvanized steel support from slab or set in cement concrete mix 1:2:4 complete as required. The connection PVC to CI shall be done with drip seal joint (item to be used for toilets). | 400 | NOS | 450 | 180000
7 | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | Hopper | SITC of G.I. inlet hopper with required inlets, The hopper shall be fabricated from 100 mm dia upto 750 mm long | Providing and fixing G.I. inlet hopper with required inlets fittings to receive waste pipes from fixtures waste. The hopper shall be fabricated from 100 mm dia upto 750 mm long G.I. heavy class pipe with welded G.I. sockets and supported through galvanized steel from slab or set in cement concrete mix 1:2:4 complete as required. The hopper shall be hot dip galvanized after fabrication and fixed to CI trap with drip seal (Cost shall be inclusive of providing 100 mm dia GI clean out plug for maintenance purpose if required as per site conditions :- for kitchen & laundry waste). | 200 | NOS | 900 | 180000
8(a) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | S.S. grating | SITC of, S.S. grating with Mosquito proof S.S. strainer, Size 125 mm x 125 mm | Providing and fixing S.S. grating with Mosquito proof S.S. strainer (cockroach trap) inlcuidng setting in floor with cement mortor to match with floor finish. | 925 | NOS | 700 | 647500
9(a) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | G.I. heavy class pipe | SITC of, G.I. heavy class pipe and fittings 40 mm dia | Providing and fixing in position G.I. heavy class pipe and fittings conforming to IS:1239 (for waste pipe from individual fixtures to floor trap & vent pipe) Including fixing at wall / ceiling level supported by galvanised clamps and hangers etc. Cutting holes in wall/floors/slabs and making good the same with cement concrete 1:2:4 complete as required (Item includes chasing and painting as per item no. 15 & 16 for kitchen & laundry). | 240 | RM | 700 | 168000
9(b) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | G.I. heavy class pipe | SITC of, G.I. heavy class pipe and fittings 50 mm dia | Providing and fixing in position G.I. heavy class pipe and fittings conforming to IS:1239 (for waste pipe from individual fixtures to floor trap & vent pipe) Including fixing at wall / ceiling level supported by galvanised clamps and hangers etc. Cutting holes in wall/floors/slabs and making good the same with cement concrete 1:2:4 complete as required (Item includes chasing and painting as per item no. 15 & 16 for kitchen & laundry). | 300 | RM | 1000 | 300000
10(a) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | PVC pipe | SITC of PVC pipe and fittings 40 mm dia | Providing & fixing PVC pipe confirm to IS -4985 and suitable for 6 kg/sqcm. This shall include connection from fixtures to floor trap, all fittings, supports from wall/ceiling, clamps & hangers cutting & making good the walls & floor where ever required. Jointing shall be done complete with PVC solvent cement. Item includes chasing as per item no. 15) | 280 | RM | 200 | 56000
10(b) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | PVC pipe | SITC of PVC pipe and fittings 50 mm dia | Providing & fixing PVC pipe confirm to IS -4985 and suitable for 6 kg/sqcm. This shall include connection from fixtures to floor trap, all fittings, supports from wall/ceiling, clamps & hangers cutting & making good the walls & floor where ever required. Jointing shall be done complete with PVC solvent cement. Item includes chasing as per item no. 15) | 1155 | RM | 250 | 288750
10( c ) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | PVC pipe | SITC of PVC pipe and fittings 63 mm dia | Providing & fixing PVC pipe confirm to IS -4985 and suitable for 6 kg/sqcm. This shall include connection from fixtures to floor trap, all fittings, supports from wall/ceiling, clamps & hangers cutting & making good the walls & floor where ever required. Jointing shall be done complete with PVC solvent cement. Item includes chasing as per item no. 15) | 500 | RM | 300 | 150000
10(d) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | PVC pipe | SITC of PVC pipe and fittings 75 mm dia | Providing & fixing PVC pipe confirm to IS -4985 and suitable for 6 kg/sqcm. This shall include connection from fixtures to floor trap, all fittings, supports from wall/ceiling, clamps & hangers cutting & making good the walls & floor where ever required. Jointing shall be done complete with PVC solvent cement. Item includes chasing as per item no. 15) | 800 | RM | 400 | 320000
11 | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) |  | SITC of straight /offset type Macfit single body push fit type WC pan connector with factory supplied spring loaded seal guard | P/Fixing straight /offset type Macfit single body push fit type WC pan connector with factory supplied spring loaded seal guard of McAlpine, UK with integral single mould sealing fins made of flexible EVA body, including bush/adaptor for use with C.I. as supplied with the pan connector (if required). | 233 | NOS | 150 | 34950
12(a) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) |  | SITC of sewage connection to kitchen equipments, appliances etc. Upto 65 mm dia | Making sewage connection to kitchen equipments, appliances etc. Including necessary fittings complete as required. | 80 | NOS | 700 | 56000
13(a) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | Air Admittance valves | SITC of Air Admittance valves with required air flow rate, including submission of design data (McAlpine/Studor). MAXI VENT 32 l/s | Providing and installing Air Admittance valves with required air flow rate, including submission of design data (McAlpine/Studor). | 10 | NOS | 6000 | 60000
13(b) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | Air Admittance valves | SITC of Air Admittance valves with required air flow rate, including submission of design data (McAlpine/Studor). MINI VENT 7.5 l/s | Providing and installing Air Admittance valves with required air flow rate, including submission of design data (McAlpine/Studor). | 10 | NOS | 5500 | 55000
14(a) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) |  | SITC of MAXI FILTRA with active carbon filters (STUDOR).100 mm dia | Providing & fixing MAXI FILTRA with active carbon filters (STUDOR). | 10 | NOS | 6000 | 60000
15(a) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | puddle flange | SITC of puddle flange to fix head in R.C.C slab. '200 mm dia bell mouth grating suitable for 100 mm dia and 600mm long MS heavy class down take pipes | Fabricating & fixing M.S. welded floor / drain / storm water collection point with puddle flange to fix head in R.C.C slab. Fabricated from 5mm thick M.S. sheet. Including removable heavy duty M.S. grating made of 50 x 3 mm thick M.S. flats (Round or Square) as per approved design. Painting with one coat 60 micron of epoxy paint over a coat of primer complete as required including connection to RWP with required fittings | 20 | NOS | 6000 | 120000
16(a) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | CI grating | SITC of CI rain water head with puddle flange to fix head in R.C.C. slab. (a) 200 mm dia bell mouth grating with 100 mm dia 600 mm long CI down take pipe | Providing and fixing CI rain water head with puddle flange to fix head in R.C.C. slab. Including removable heavy duty dome type CI grating and CI Jaali with ring of approved design including connection to the RWP with required fittings | 10 | NOS | 9000 | 90000
16(b) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | CI grating | SITC of CI rain water head with puddle flange to fix head in R.C.C. slab.(b)300 mm dia bell mouth grating with 150 mm dia 600mm long CI down take pipe | Providing and fixing CI rain water head with puddle flange to fix head in R.C.C. slab. Including removable heavy duty dome type CI grating and CI Jaali with ring of approved design including connection to the RWP with required fittings | 10 | NOS | 10000 | 100000
17 | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | `Khurras' | SITC of rain water `Khurras' size 500x500 mm of required depth | Providing & fixing rain water `Khurras' size 500x500 mm of required depth with lead flashing around the pipe with one piece lead sheet of 3 mm thick set on a layer of cold bitumen. Including Heavy duty CI/MS grating with vertical flats as per drawing complete as required. | 40 | NOS | 1000 | 40000
18 | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | `Khurras' | SITC of khurras, 100mm dia balcony drain with grating of approved design with 300mm x 300mm khurras | Providing and fixing 100mm dia balcony drain with grating of approved design with 300mm x 300mm khurras and lead flashing complete as required. | 20 | NOS | 700 | 14000
19(a) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | paint | SITC of two coats of Synthetic enamel paint of approved shade as per pipe colour, 80 mm dia | Providing two coats of Synthetic enamel paint of approved shade as per pipe colour code over a coat of primer. Including painting of legends with direction arrow as per the approval of the Architects / Consultants. | 925 | RM | 90 | 83250
19(b) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | paint | SITC of two coats of Synthetic enamel paint of approved shade as per pipe colour, 100 mm dia | Providing two coats of Synthetic enamel paint of approved shade as per pipe colour code over a coat of primer. Including painting of legends with direction arrow as per the approval of the Architects / Consultants. | 4100 | RM | 100 | 410000
19( c ) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | paint | SITC of two coats of Synthetic enamel paint of approved shade as per pipe colour, 150 mm dia | Providing two coats of Synthetic enamel paint of approved shade as per pipe colour code over a coat of primer. Including painting of legends with direction arrow as per the approval of the Architects / Consultants. | 1450 | RM | 150 | 217500
20(a) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | COP | SITC of clean out plug jointing with G.I. heavy class pipe , For 100mm dia pipe | Providing and fixing blank flange clean out plug jointing with G.I. heavy class pipe and blank flange complete with flange joint. socket jointing with drip seal to CI pipe / CILA pipe complete as required. | 165 | NOS | 1100 | 181500
20(b) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | COP | SITC of clean out plug jointing with G.I. heavy class pipe , For 150mm dia pipe | Providing and fixing blank flange clean out plug jointing with G.I. heavy class pipe and blank flange complete with flange joint. socket jointing with drip seal to CI pipe / CILA pipe complete as required. | 80 | NOS | 1700 | 136000
20( c ) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | COP | SITC of clean out plug jointing with G.I. heavy class pipe , For 200mm dia pipe | Providing and fixing blank flange clean out plug jointing with G.I. heavy class pipe and blank flange complete with flange joint. socket jointing with drip seal to CI pipe / CILA pipe complete as required. | 15 | NOS | 5025 | 75375
21(a) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | COP | SITC of Brass clean out plug with S.S. screw, GI heavy class pipe, For 100mm dia pipe | Providing and fixing Brass clean out plug with S.S. screw, GI heavy class pipe and socket jointing with jointing to pipes complete as required | 10 | NOS | 1500 | 15000
21(b) | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | COP | SITC of Brass clean out plug with S.S. screw, GI heavy class pipe, For 150mm dia pipe | Providing and fixing Brass clean out plug with S.S. screw, GI heavy class pipe and socket jointing with jointing to pipes complete as required | 30 | NOS | 5500 | 165000
22 | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | Trap | SITC of portable type grease trap fixing below counter sink. | Providing and fixing portable type grease trap fixing below counter sink. | 5 | NOS | 1200 | 6000
23 | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | grease separator plant | SITC of grease separator plant as per DIN4040/pr EN1825 with direct suction pipe DN65 | Providing and fixing grease separator plant as per DIN4040/pr EN1825 with direct suction pipe DN65 and hose quick coupling story B75 with integrated sludge trap of 400 litres capacity of polyethylene (PE-HD), round shape without partition segment design for free standing installation with outlet / inlet pipe of dia 100mm. Size NS 4 for 400 meals per day kitchen working 15 hours a day. Including glass window, water inlet point, sludge transfer pump and sampling device complete including fully automatic cleaning maceratoring and pumping of grease separator waste as required as per manufacturer's specifications. It should be fully factory assembled system with certification. | 1 | NOS | 1023000 | 1023000
24 | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | grease separator plant | SITC of grease separator plant as per DIN4040/pr EN1825 with direct suction pipe DN65 | Providing and fixing grease separator plant as per DIN4040/pr EN1825 with direct suction pipe DN65 and hose quick coupling story B75 with integrated sludge trap of 1500 litres capacity of polyethylene (PE-HD), round shape without partition segment design for free standing installation with outlet / inlet pipe of dia 200mm. Size NS15 for 1600 meals per day kitchen working 15 hours a day. Including glass window, water inlet point, sludge transfer pump and sampling device complete including fully automatic cleaning maceratoring and pumping of grease separator waste as required as per manufacturer's specifications. It should be fully factory assembled system with certification. | 3 | NOS | 2226787 | 6680361
25 | PLUMBING WORK | INTERNAL DRAINAGE (SOIL, WASTE, VENT AND RAIN WATER PIPES) | Oil and Fuel separator | SITC of basement parking for oil and fuel separator of capacity NS 1.5 certified as per EN 858 | Providing and fixing oil and fuel separator of capacity NS 1.5 certified as per EN 858 for basement parking. | 7 | NOS | 151725 | 1062075
1(a) | PLUMBING WORK | EXTERNAL DRAINAGE | DWC HDPE Pipes | SITC of heavy class DWC HDPE pipes SN 8 confirming to IS: 16098 suitable for working pressure of 6 Kg/sqcm for drainage system 150 mm dia | Providing, fixing, jointing & testing in position the following heavy class DWC HDPE pipes SN 8 confirming to IS: 16098 suitable for working pressure of 6 Kg/sqcm for drainage system. Including pipe to be laid below ground in trenches upto required depth, including excavation in all kind of soil (hard rock) dewatering, refilling, watering, ramming and shfiting shall be done by the contractor of excavated material within the site limit as directed by site incharge, making good the same complete as required. | 250 | RM | 681 | 170250
1(b) | PLUMBING WORK | EXTERNAL DRAINAGE | DWC HDPE Pipes | SITC of heavy class DWC HDPE pipes SN 8 confirming to IS: 16098 suitable for working pressure of 6 Kg/sqcm for drainage system 200 mm dia | Providing, fixing, jointing & testing in position the following heavy class DWC HDPE pipes SN 8 confirming to IS: 16098 suitable for working pressure of 6 Kg/sqcm for drainage system. Including pipe to be laid below ground in trenches upto required depth, including excavation in all kind of soil (hard rock) dewatering, refilling, watering, ramming and shfiting shall be done by the contractor of excavated material within the site limit as directed by site incharge, making good the same complete as required. | 160 | RM | 1200 | 192000
1( c ) | PLUMBING WORK | EXTERNAL DRAINAGE | DWC HDPE Pipes | SITC of heavy class DWC HDPE pipes SN 8 confirming to IS: 16098 suitable for working pressure of 6 Kg/sqcm for drainage system 250 mm dia | Providing, fixing, jointing & testing in position the following heavy class DWC HDPE pipes SN 8 confirming to IS: 16098 suitable for working pressure of 6 Kg/sqcm for drainage system. Including pipe to be laid below ground in trenches upto required depth, including excavation in all kind of soil (hard rock) dewatering, refilling, watering, ramming and shfiting shall be done by the contractor of excavated material within the site limit as directed by site incharge, making good the same complete as required. | 50 | RM | 1300 | 65000
1(d) | PLUMBING WORK | EXTERNAL DRAINAGE | DWC HDPE Pipes | SITC of heavy class DWC HDPE pipes SN 8 confirming to IS: 16098 suitable for working pressure of 6 Kg/sqcm for drainage system 300 mm dia | Providing, fixing, jointing & testing in position the following heavy class DWC HDPE pipes SN 8 confirming to IS: 16098 suitable for working pressure of 6 Kg/sqcm for drainage system. Including pipe to be laid below ground in trenches upto required depth, including excavation in all kind of soil (hard rock) dewatering, refilling, watering, ramming and shfiting shall be done by the contractor of excavated material within the site limit as directed by site incharge, making good the same complete as required. | 80 | RM | 1800 | 144000
1( e ) | PLUMBING WORK | EXTERNAL DRAINAGE | DWC HDPE Pipes | SITC of heavy class DWC HDPE pipes SN 8 confirming to IS: 16098 suitable for working pressure of 6 Kg/sqcm for drainage system 400 mm dia | Providing, fixing, jointing & testing in position the following heavy class DWC HDPE pipes SN 8 confirming to IS: 16098 suitable for working pressure of 6 Kg/sqcm for drainage system. Including pipe to be laid below ground in trenches upto required depth, including excavation in all kind of soil (hard rock) dewatering, refilling, watering, ramming and shfiting shall be done by the contractor of excavated material within the site limit as directed by site incharge, making good the same complete as required. | 50 | RM | 2590 | 129500
2(a) | PLUMBING WORK | EXTERNAL DRAINAGE | Civil | SITC of uPVC / HDPE pipes for cement concrete 1:4:8, 150 mm dia (with 150 mm thick bedding) | Providing & laying cement concrete 1:4:8 for uPVC / HDPE pipes for storm water system including bedding and haunches upto the center of pipe as per approved working drawings including shuttering & timbering complete as required | 250 | RM | 400 | 100000
2(b) | PLUMBING WORK | EXTERNAL DRAINAGE | Civil | SITC of uPVC / HDPE pipes for cement concrete 1:4:8, 200 mm dia (with 150 mm thick bedding) | Providing & laying cement concrete 1:4:8 for uPVC / HDPE pipes for storm water system including bedding and haunches upto the center of pipe as per approved working drawings including shuttering & timbering complete as required | 160 | RM | 600 | 96000
2( c ) | PLUMBING WORK | EXTERNAL DRAINAGE | Civil | SITC of uPVC / HDPE pipes for cement concrete 1:4:8, 250 mm dia (with 150 mm thick bedding) | Providing & laying cement concrete 1:4:8 for uPVC / HDPE pipes for storm water system including bedding and haunches upto the center of pipe as per approved working drawings including shuttering & timbering complete as required | 50 | RM | 900 | 45000
2(d) | PLUMBING WORK | EXTERNAL DRAINAGE | Civil | SITC of uPVC / HDPE pipes for cement concrete 1:4:8, 300 mm dia (with 150 mm thick bedding) | Providing & laying cement concrete 1:4:8 for uPVC / HDPE pipes for storm water system including bedding and haunches upto the center of pipe as per approved working drawings including shuttering & timbering complete as required | 80 | RM | 1100 | 88000
2( e ) | PLUMBING WORK | EXTERNAL DRAINAGE | Civil | SITC of uPVC / HDPE pipes for cement concrete 1:4:8, 400 mm dia (with 150 mm thick bedding) | Providing & laying cement concrete 1:4:8 for uPVC / HDPE pipes for storm water system including bedding and haunches upto the center of pipe as per approved working drawings including shuttering & timbering complete as required | 50 | RM | 1300 | 65000
3(a) | PLUMBING WORK | EXTERNAL DRAINAGE | Chamber | SITC of Brick manhole, Inside size 90x80 cm upto 60 cm deep | Constructing Brick manhole of the following sizes in with complete construction details as per manufacturer including excavation, in all kind of soil including dewatering, refilling, watering, ramming and shifting shall be done by the contractor of excavated material within the site limit as directed by site incharge, making good the same complete as required. | 25 | NOS | 10000 | 250000
3(b) | PLUMBING WORK | EXTERNAL DRAINAGE | Chamber | SITC of Brick manhole, Extra over 'a' above for depth exceeding 60 cm to 90cm | Constructing Brick manhole of the following sizes in with complete construction details as per manufacturer including excavation, in all kind of soil including dewatering, refilling, watering, ramming and shifting shall be done by the contractor of excavated material within the site limit as directed by site incharge, making good the same complete as required. | 5 | RM | 4000 | 20000
3( c ) | PLUMBING WORK | EXTERNAL DRAINAGE | Chamber | SITC of Brick manhole, Inside size 120 cm x 90 cm upto 90 cm deep | Constructing Brick manhole of the following sizes in with complete construction details as per manufacturer including excavation, in all kind of soil including dewatering, refilling, watering, ramming and shifting shall be done by the contractor of excavated material within the site limit as directed by site incharge, making good the same complete as required. | 80 | NOS | 13000 | 1040000
3(d) | PLUMBING WORK | EXTERNAL DRAINAGE | Chamber | SITC of Brick manhole, Inside size 120 cm x 90 cm upto 90 cm deep | Constructing Brick manhole of the following sizes in with complete construction details as per manufacturer including excavation, in all kind of soil including dewatering, refilling, watering, ramming and shifting shall be done by the contractor of excavated material within the site limit as directed by site incharge, making good the same complete as required. | 8 | RM | 5500 | 44000
3( e ) | PLUMBING WORK | EXTERNAL DRAINAGE | Chamber | SITC of Brick manhole, Inside size 140cm x 90 cm for depth 250 cm | Constructing Brick manhole of the following sizes in with complete construction details as per manufacturer including excavation, in all kind of soil including dewatering, refilling, watering, ramming and shifting shall be done by the contractor of excavated material within the site limit as directed by site incharge, making good the same complete as required. | 130 | NOS | 6000 | 780000
3(f) | PLUMBING WORK | EXTERNAL DRAINAGE | Chamber | SITC of Brick manhole, Extra over 'e' above for depth exceeding 240cm to 500cm deep | Constructing Brick manhole of the following sizes in with complete construction details as per manufacturer including excavation, in all kind of soil including dewatering, refilling, watering, ramming and shifting shall be done by the contractor of excavated material within the site limit as directed by site incharge, making good the same complete as required. | 10 | RM | 5600 | 56000
4 | PLUMBING WORK | EXTERNAL DRAINAGE | Chamber Cover | SITC of HDPE heavy duty perforated heavy duty manhole cover of 605 mm dia | Providing and fixing HDPE heavy duty perforated heavy duty manhole cover of 605 mm dia with lifting lugs and frame for storm water manholes. | 50 | NOS | 7000 | 350000
5(a) | PLUMBING WORK | EXTERNAL DRAINAGE | Civil | SITC of basins in brick work with bricks of class designation 75 in cement mortar 1:5, Internal size 600x450x600 mm | Constructing catch basins in brick work with bricks of class designation 75 in cement mortar 1:5 (1 cement, 5 finesand). Inside plastering 12mm thick with cement mortar 1:3 (1 cement, 3 coarse sand) and 'rough plaster on outside with a floating coat of neat cement on both sides with necessary concrete foundation 1:4:8 (1 cement, 4 coarse sand, 8 graded stone aggregated 40mm nominal size). Including providing & fixing the Heavy duty HDPE grating with frame on PCC. Necessary excavation in all kind of soil, dewatering, refilling, watering, ramming and shfiting shall be done by the contractor of excavated material within the site limit as directed by site incharge, making good the same complete as required. | 40 | NOS | 8000 | 320000
5(b) | PLUMBING WORK | EXTERNAL DRAINAGE | Civil | SITC of basins in brick work with bricks of class designation 75 in cement mortar 1:5 , Extra over `a' depth exceeding 600mm | Constructing catch basins in brick work with bricks of class designation 75 in cement mortar 1:5 (1 cement, 5 finesand). Inside plastering 12mm thick with cement mortar 1:3 (1 cement, 3 coarse sand) and 'rough plaster on outside with a floating coat of neat cement on both sides with necessary concrete foundation 1:4:8 (1 cement, 4 coarse sand, 8 graded stone aggregated 40mm nominal size). Including providing & fixing the Heavy duty HDPE grating with frame on PCC. Necessary excavation in all kind of soil, dewatering, refilling, watering, ramming and shfiting shall be done by the contractor of excavated material within the site limit as directed by site incharge, making good the same complete as required. | 3 | RM | 3500 | 10500
1 | PLUMBING WORK | PUMPS, EQUIPMENT AND ELECTRICAL PANEL | Pumps | SITC of domestic hydropneumatic system, 'Pump capacity - 180 LPM,'Head - 80 meter, RPM - 2900 | Supply, installing, testing and commissioning of compact self contained skid mounted factory fitted including panel domestic hydropneumatic system (For upper zone),(a)Vertical in line pumps 4 Nos complete in S.S. coupled with IE 3 TEFC motor. 'Pump capacity - 180 LPM,'Head - 80 meter, RPM - 2900, (b)Electric control panel with frequency convertor. Each pump will have independent VFD,( c)Logic controller relays, (d)Pressure switch & pressure transmitter,(e)Electrical wiring, cabling with cable tray as specified from panel to pumps, (f)2 Nox. x 300 litre vessels with interchangeable butyl rubber membrane suitable for working pressure of 15 kg/sqcm,(g)Ball valves, butterfly valves, NRV's on suction and discharge header, (h)Pressure gauge with valve on each suction and discharge pipe of pump,Suction and discharge(i)Base frame and antivibration arrangement of approved design (j)header complete in S.S. with dead end flanges,Hydropneumatic system as described above for domestic water supply | 1 | SET | 1800000 | 1800000
| PLUMBING WORK | PUMPS, EQUIPMENT AND ELECTRICAL PANEL | Pumps | SITC of panel domestic hydropneumatic system, 'Pump capacity - 190 LPM,'Head - 55 meter, RPM - 2900 | Supply, installing, testing and commissioning of compact self contained skid mounted factory fitted including panel domestic hydropneumatic system (For lower zone) (a) 'Pump capacity - 190 LPM,'Head - 55 meter, RPM - 2900(b)Electric control panel with frequency convertor. Each pump will have independent VFD.(c)Logic controller relays(d)Pressure switch & pressure transmitter(e)Electrical wiring, cabling with cable tray as specified from panel to pumps(f)2 Nox. x 300 litre vessels with interchangeable butyl rubber membrane suitable for working pressure of 15 kg/sqcm(g)Ball valves, butterfly valves, NRV's on suction and discharge header (h)Pressure gauge with valve on each suction and discharge pipe of pump(i)Base frame and antivibration arrangement of approved design(j)Suction and discharge header complete in S.S. with dead end flanges,Hydropneumatic system as described above for domestic water supply | 1 | SET | 1750000 | 1750000
| PLUMBING WORK | PUMPS, EQUIPMENT AND ELECTRICAL PANEL | Pumps | SITC of centrifugal pump complete in SS, Location: Plumbing Plant Room, Flow rate: 420 LPM, RPM : 2900 | Supplying, installing, testing and commissioning of vertical multistage centrifugal pump complete in SS. Each pump shall have TEFC three phase electric motor IE3. Pump shall be provided with mechanical seal. The pump shall be suitable for auto/ manual operation.Application: Filter feed pumps -2 NOS (1W+1SB), Location: Plumbing Plant Room, Flow rate: 420 LPM, RPM : 2900 | 2 | NOS | 180000 | 360000
| PLUMBING WORK | PUMPS, EQUIPMENT AND ELECTRICAL PANEL | Pumps | SITC of sewage sump pumps (2W) with cutter, Location: Sump of basement, Flow rate: 250 LPM, Head: 15 Mts | Supply, installing, testing and commissioning of 2 Nos. submersible non clog sewage sump pumps (2W) with cutter, with 3 phase motor with all necessary protection and the mechanical seal etc. including electrical starter panel for both pumps, cabling upto motor as per manufacturer specifications. Automation and dry protection of pumps by float level switch complete as required, Location: Sump of basement, Flow rate: 250 LPM, Head: 15 Mts,Solid Handling: 40mm | 1 | SET | 350000 | 350000
| PLUMBING WORK | PUMPS, EQUIPMENT AND ELECTRICAL PANEL | Pumps | SITC of water sump pumps, Location: Sump of basement, Flow rate: 200 LPM, Head: 15 Mts | Supply, installing, testing and commissioning of 2 Nos. submersible non clog storm water sump pumps with 3 phase motor with all necessary protection and the mechanical seal etc. including electrical starter panel for both pumps, cabling upto motor as per manufacturer specifications. Automation and dry protection of pumps by float level switch complete as required, Location: Sump of basement, Flow rate: 200 LPM, Head: 15 Mts,Solid Handling: 10mm | 4 | SET | 330000 | 1320000
| PLUMBING WORK | CONTROL PANELFOR PLUMBING EQUIPMENTS AT BASEMENT LEVEL | Control Panel | SITC of CRCA sheet steel control panel, fabricated out of 2mm thick for structural members (load bearing members) and 1.6mm thick for doors & covers | Design, fabrication, loading, unloading as directed by Engineer-in-charge, supply, installation, testing and commissioning of the following intergrated, cubicle type, dead front, extensible CRCA sheet steel control panel fabricated out of 2mm thick for structural members (load bearing members) and 1.6mm thick for doors & covers (non load bearing members), free standing floor mounted, dust and vermin proof with reinforcement of suitable size MS angle, channel `T', flats, cable gland plates shall be provided on top as well as bottom. Treatment of panel as per technical specifications. The panel shall be suitable for 500 volts, 50 cycles, 4 wire supply. Quoted price shall also include 25 mm thick rubber mats, wiring, cabling, cable tray, control wiring and copper earthing from control panel to various equipment like motor starters, pump motor, etc. The panel shall have separate compartments for bus bar and cable alleys.'The following components and accessories shall be mounted within each control panel.'(A) One No. 100 amps TPN incoming MCB complete with the following:'(i.) 0-500 volts 96x96 mm voltmeter with selector switch and MCBs.(ii.) 0-100 amps 96x96 mm ammeter with 100/5 amps ratio CT's and selector switch (iii.)Phase indicating lamps with toggle switches.(iv.) Indication lamps for ON/OFF/TRIP status of motors.Aluminium bus bar sleeves type, rated at 200 amps for three phase & neutral. (B)Aluminium bus bar sleeves type, rated at 200 amps for three phase & neutral. (C) OUTGOING FEEDERS / STARTERS:(1)63A TPN MCB outgoing feeder suitable for 22.5 HP hydropneumatic pump panel(2)63A TPN MCB outgoing feeder suitable for 20 HP hydropneumatic pump panel(3)40 A 4P MCB with DOL starter with over load relay and single phase preventer each suitable for 5 HP motor for filter feed pumps pumps(4)40A TPN MCB outgoing feeder suitable for 5 HP sump pump panel (5)Spares:-a. 63 Amps MCCB - 1 No, b. 40 Amps MCB - 2 No, Control Panel as described above. | 1 | SET | 150000 | 150000
63403301