## Summary
NAME OF WORK -PROJECT :- PROPOSED CONSTRUCTION OF BANK, OFFICE BUILDING, RESIDENTIAL ACCOMODATION AT PIMPRI, PUNE FOR BANK OF INDIA
S.No. | Description | BOQ Amount | Remark
1 | Civil Work | 0
2 | Plumbing Work | 0 | #DIV/0!
3 | Fire Fighting Work | 5920283.1
4 | Electrical Work + HVAC | 0 |  | 0
5 | Conference Room | 0 | 6000000
6 | Furniture | 0 | 15000000
| Total Amount DSR-2021 | 26920283.1
| Add 6% GST | 1615216.986
| Including 18% GST | 28535500.086
26920283.1
357750000
1994.095

## Civil & Plumbing BOQ
NAME OF WORK -PROJECT :- PROPOSED CONSTRUCTION OF BANK, OFFICE BUILDING, RESIDENTIAL ACCOMODATION AT PIMPRI, PUNE FOR BANK OF INDIA
BILL OF QUANTITY
Item No. | DSR-21 | Particulars | Quantity | Unit | Rate (RS.) | Amount ( Rs. )
|  | DISMANTALLING |  |  | dsr 21
1 | L.S. | DISMANTALLING:- Dismantling mechanically or/ and manually, existing structures/ Buildings on site and disposal of all unserviceable material , debris, etc. arising from the dismantalling and deposit the same at dumping grounds approved by statutory authorities including loading, unloading and transportation etc complete. In no case stacking/ storing of this material on site shall be allowed. All safety/ precautionary measures shall be taken during demolishing. Contractor shall be responsible for all legal and financial consequences of any accident, mishap during demolishing.Including any statutory permission / permissios reuired for dumping the material / debris etc. complete. | 1 | Job |  | 5000000
CIVIL WORK
1 | 2.8.1 | Excavation for foundation in earth, soil of all types, sand, gravel and soft murum, including removing the excavated material up to a distance of 50 m. beyond the building area and stacking and spreading as directed, dewatering, preparing the bed for the foundation and necessary back filling, ramming, watering including shoring and strutting etc. complete. Including all lead & lift. Cart away all unwanted excavated material, debris, etc. arising from the excavation at site and deposit the same at dumping grounds approved by statutory authorities.By Mechanical Means. | 1032.65 | Cum |  | 0 | 688.4333
2 |  | Excavation for foundation in hard murum including removing the excavated material upto distance of 50 metres beyond the building area and stacking and spreading as directed, dewatering, preparing the bed for the foundation and necessary back filling, ramming, watering including shoring and strutting etc. complete.Including all lead & lift. Cart away all unwanted excavated material, debris, etc. arising from the excavation at site and deposit the same at dumping grounds approved by statutory authorities. By Mechanical Means. | 1032.65 | Cu.M |  | 0
3 | 2.9.1 | Excavation for foundation in Soft rock and old cement or lime masonry foundations including removing the excavated material upto a distance of 50 metres beyond the building area and stacking as directed, including dewatering, preparing the bed for the foundation and necessary back filling with available earth /murum, ramming, watering including shoring and strutting etc. complete.Including all lead & lift. Cart away all unwanted excavated material, debris, etc. arising from the excavation at site and deposit the same at dumping grounds approved by statutory authorities. By Mechanical Means. | 3605.73 | Cu.M |  | 0
4 | 2.9.3 | Excavation for foundation in Hard rock by chiselling, wedging, line drilling, etc. including trimming and levelling the bed, removing the excavated material upto a distance of 50 metres beyond the building area stacking as directed, dewatering and back filling with available earth/ murum watering, ramming etc. complete.Including all lead & lift. Cart away all unwanted excavated material, debris, etc. arising from the excavation at site and deposit the same at dumping grounds approved by statutory authorities. By Mechanical Means. | 7211.46 | Cu.M |  | 0
5 | 2.9.2 | Excavation for foundation in Hard-rock by controlled blasting including trimming and leveling the bed by chiselling where necessary and removing the excavated material and stacking it in measurable heaps within a distance of 50 metres. from the building area including dewatering and back filling with available earth soil /murum watering, ramming etc. complete. Including all lead & lift. Cart away all unwanted excavated material, debris, etc. arising from the excavation at site and deposit the same at dumping grounds approved by statutory authorities.By Mechanical Means Including all necessary satutary permissions. | 2296.88 | Cu.M |  | 0
6 | 2.25 | Filling in plinth and floors with approved excavated material in 15cm. to 20cm. Layers including watering and compacting etc. complete. | 2065.3 | Cu.M |  | 0
7 | 2.25(a) | Filling in plinth and floors with contractors material / brought from outside and approved by Engineer incharge in layers of 15 cm to 20 cm including watering and compaction etc. complete. | 12834.85 | Cu.M |  | 0 | 15179.39 | 279.24 | 12834.85
8 | 16.3.1 | Providing dry/ trap/ granite/ quartzite/ gneiss rubble stone soling 15 cm to 20 cm thick including hand packing and compacting etc. complete. | 70.51 | Cu.M |  | 0
BD-Antitermite Treatment
9 | 2.35.3.1 | Providing preconstructional antitermite treatment as per I.S. 6313 (Part-II) by treating the bottom surface and sides of excavation at the rate of 5 litres of emulsion concentrate of 1.0 percent of chlorophyrifos per square meter of surface area covering 10 years guarantee on bond paper. | 3012.71 | Sq.M |  | 0
10 | 2.35.3.1 | Providing preconstructional antitermite treatment as per I.S. 6313 (Part-II) treatment by treating the backfill in immediate contact with foundation at the rate of 5 litres of emulsion concentrate of 1.0 percent of clorophyrifos per square metre of vertical surface area covering 10 years guarantee on bond paper. | 1406.5 | Sq.M |  | 0
11 | 2.35.3.1 | Providing preconstructional antitermite treatment as per I.S.6313 (Part-II) by treating the top surface of plinth filling at the rate of 5 litres of emulsion concentrate at 1.0 percent of clorophyrifos per square metre of surface area covering ten years guarantee on bond paper. | 1762.8 | Sq.M |  | 0
BDE- Plain cement concrete
12 | 4.20.1.2 | Providing and laying Cast in situ / Ready Mix cement concrete in M15 of trap / granite / quartzite / gneiss metal for bed blocks, foundation blocks and such other items including bailing out water, Steel centering, form work, laying / pumping, compacting, roughening them if special finishis to be provided, finishing uneven and honey combed surface and curing etc. complete. The Cement Mortar 1:3 plaster is considered for rendering uneven and honey combed surface only. Newly laid concrete shall be covered by gunny bag, plastic, tarpaulin etc. (Wooden centering will not be allowed.), with fully automatic microprocess or based PLC withot SCADA enabled reversible DrumType mixer / concrete Batch mix plant (Pan mixer) etc. complete. With fine aggregate (Crushed sand VSI Grade) | 209.53 | Cu.M |  | 0
BDF- Reinforced cement concrete
13 | 4.20.1.4 | Providing and laying Cast in situ / Ready Mix cement concrete M-30 of trap / granite / quartzite / gneiss metal for R.C.C. work in foundations like raft, strip foundations,grill age and footings of R.C.C. columns and steel stanchions etc. including bailing out water, Steel centering, formwork, cover blocks, laying / pumping, compaction and curing roughening the surface if special finishis to be provided (Excluding reinforcement and structural steel)etc.complete,with fully automatic microprocess or based PLC without SCADA enabled reversible Drum Type mixer / concrete Batch mix plant (Pan mixer)etc.complete.With fine aggregate (Crushed sand VSI Grade) | 849.01 | Cu.M |  | 0
| 5.9.1 | Formwork for foundation | 2525.8047 | Sq.M |  | 0 | 297.1535 |  |  | 7216.585
| 5.9.2 | Wall | 1082.4877 | Sq.M |  | 0 | 127.3515
| 5.9.3 | slab | 2164.9755 | Sq.M |  | 0 | 424.505
| 5.9.5 | beam | 1443.317 | Sq.M |  | 0 | 424.505
14 |  | Providing and laying Cast in situ / Ready Mix cement concrete M-50 of trap / granite / quartzite /gneiss metal for R.C.C. columns as per detailed designs and drawings or as directed including steel centering, formwork, cover blocks, laying/ pumping, compaction finishing the formed surfaces with cement mortar 1:3 of sufficient minimum thickness to give a smoot hand even surface or roughening if special finish is to be provided and curing etc. complete, (Excluding reinforcement and structural steel). with fully automatic microprocess or based PLC without SCADA enabled reversible Drum Type mixer/ concrete Batch mix plant (Pan mixer) etc. complete. With fine aggregate (Crushed sand VSI Grade) | [6 empty] | Rate
| 5.33.1.5 | Footing Top to Basement 2 Level | 37.68 | Cu.M |  | 0 | 9.13 | 344.0184 | 804.25 | 276676.7982
|  | Basement 2 | 74.66 | Cu.M |  | 0 | 9.13 | 681.6458 | 804.25 | 548213.6347
|  | Basement 1 | 57.59 | Cu.M |  | 0 | 9.13 | 525.7967 | 804.25 | 422871.996
| 5.33.2.5 | Ground Floor | 69.78 | Cu.M |  | 0 | 9.13 | 637.0914 | 804.25 | 512380.7585
|  | First Floor | 39.53 | Cu.M |  | 0 | 9.13 | 360.9089 | 804.25 | 290260.9828
| 5.9.6 | Column Shuttering | 344.0184 | Sq.M |  | 0
|  |  | 681.6458 | Sq.M |  | 0
|  |  | 525.7967 | Sq.M |  | 0
|  |  | 637.0914 | Sq.M |  | 0
|  |  | 360.9089 | Sq.M |  | 0
| 4.1.8 | Pcc of footing | 250 | Cu.M |  | 0
| 4.3.1 | Pcc of footing Shuttering | 875 | Sq.M |  | 0
15 |  | Providing and laying Cast in situ/Ready Mix cement concrete M-40 of trap /granite /quartzite/ gneiss metal for R.C.C. columns as per detailed designs and drawing or as directed including steel centering, formwork, cover blocks, laying/pumping, compaction finishing the formed surfaces with cement mortar 1:3 of sufficient minimum thickness to give a smooth and even surface or roughening if special finish is to be provided and curing etc. complete,(Excluding reinforcement and structural steel).with fully automatic micro processor based PLC with SCADA enabled reversible Drum Type mixer/ concrete Batch mix plant (Pan mixer) etc. complete. With fine aggregate (Crushed sand VSI Grade) | [7 empty] | 2050404.1701
| 5.33.2.4 | Ground Floor | 18.59 | Cu.M |  | 0
|  | Second Floor | 32.94 | Cu.M |  | 0
|  | Third Floor | 32.67 | Cu.M |  | 0
|  | Fourth Floor | 34.16 | Cu.M |  | 0
| 5.33.2.4 + 5.38 | Fifth Floor | 35.64 | Cu.M |  | 0
|  | Sixth Floor | 29.7 | Cu.M |  | 0
|  | Seventh Floor | 29.7 | Cu.M |  | 0
|  | Eighth Floor | 29.7 | Cu.M |  | 0
|  | Terrace Floor | 15.66 | Cu.M |  | 0
|  | Formwork |  |  |  |  | 2362.4788
| 5.9.6 | Ground Floor | 169.7267 | Sq.M |  | 0
| 5.9.6 | Second Floor | 300.7422 | Sq.M |  | 0
| 5.9.6 | Third Floor | 298.2771 | Sq.M |  | 0
| 5.9.6 | Fourth Floor | 311.8808 | Sq.M |  | 0
| 5.9.6 | Fifth Floor | 325.3932 | Sq.M |  | 0
| 5.9.6 | Sixth Floor | 271.161 | Sq.M |  | 0
| 5.9.6 | Seventh Floor | 271.161 | Sq.M |  | 0
| 5.9.6 | Eighth Floor | 271.161 | Sq.M |  | 0
| 5.9.6 | Terrace Floor | 142.9758 | Sq.M |  | 0
2362.4788
16 |  | Providing and laying Cast in situ / Ready Mix cement concrete in M-50 of trap / granite /quartzite /gneiss metal for R.C.C. beams and lintels as per detailed designs and drawings or as directed including steel centering, formwork, cover blocks, laying / pumping, compaction and roughening the surface if special finish is to be provided and curing etc. complete. (Excluding reinforcement and structural steel). with fully automatic microprocess or based PLC without SCADA enabled reversible Drum Type mixer / concrete Batch mix plant (Pan mixer)etc.complete. With fine aggregate (Crushed sand VSI Grade)
| 5.33.1.5 | Basement 2 Floor | 37.68 | Cu.M |  | 0
|  | Basement 1 Floor | 64.12 | Cu.M |  | 0
| 5.33.2.5 | Ground Floor | 94.52 | Cu.M |  | 0
|  | First Floor | 86.57 | Cu.M |  | 0
Formwork
| 5.9.5 | Basement 2 Floor | 244.92 | Sq.M |  | 0
|  | Basement 1 Floor | 416.78 | Sq.M |  | 0
|  | Ground Floor | 614.38 | Sq.M |  | 0
|  | First Floor | 562.705 | Sq.M |  | 0
17 |  | Providing and laying Cast in situ / Ready Mix cement concrete in M-40 of trap / granite /quartzite /gneiss metal for R.C.C. beams and lintels as per detailed designs and drawings or as directed including steel centering, formwork, cover blocks, laying / pumping, compaction and roughening the surface if special finish is to be provided and curing etc. complete. (Excluding reinforcement and structural steel). with fully automatic microprocess or based PLC without SCADA enabled reversible Drum Type mixer / concrete Batch mix plant (Pan mixer)etc.complete. With fine aggregate (Crushed sand VSI Grade)
| 5.33.2.4 | Ground Floor | 22.36 | Cu.M |  | 0
|  | Second Floor | 42 | Cu.M |  | 0
|  | Third Floor | 58.94 | Cu.M |  | 0
|  | Fourth Floor | 58.94 | Cu.M |  | 0
| 5.33.2.4 + 5.38 | Fifth Floor | 58.94 | Cu.M |  | 0
|  | Sixth Floor | 40.45 | Cu.M |  | 0
|  | Seventh Floor | 47.61 | Cu.M |  | 0
|  | Eighth Floor | 47.61 | Cu.M |  | 0
|  | Top Terrace | 48.48 | Cu.M |  | 0
| 5.9.5 | Ground Floor | 208.1716 | Sq.M |  | 0
| 5.9.6 | Second Floor | 391.02 | Sq.M |  | 0
| 5.9.7 | Third Floor | 548.7314 | Sq.M |  | 0
| 5.9.8 | Fourth Floor | 548.7314 | Sq.M |  | 0
| 5.9.9 | Fifth Floor | 548.7314 | Sq.M |  | 0
| 5.9.10 | Sixth Floor | 376.5895 | Sq.M |  | 0
| 5.9.11 | Seventh Floor | 443.2491 | Sq.M |  | 0
| 5.9.12 | Eighth Floor | 443.2491 | Sq.M |  | 0
| 5.9.13 | Terrace Floor | 451.3488 | Sq.M |  | 0
18 |  | Providing and laying Cast in situ / Ready Mix cement concrete M-50 of trap / granite / quartzite /gneiss metal for R.C.C. slabs and landings as per detailed designs and drawings including steel centering, form work, cover blocks, laying / pumping, compaction finishing the formed surfaces with cement mortar 1:3 of sufficient minimum thickness to give a smoot hand even surface or roughening if special finish is to be provided and curing etc. complete, (Excluding reinforcement and structural steel). with fully automatic microprocess or based PLC without SCADA enabled reversible Drum Type mixer/ concrete Batch mix plant (Pan mixer) etc. complete. With fine aggregate (Crushed sand VSI Grade)
| 5.33.1.5 | Basement 2 | 107.55 | Cu.M |  | 0
|  | Basement 1 | 162.94 | Cu.M |  | 0
| 5.33.2.5 | Ground Floor | 208.43 | Cu.M |  | 0
|  | First Floor | 196 | Cu.M |  | 0
Formwork
| 5.9.3 | Basement 2 | 784.0395 | Sq.M |  | 0
|  | Basement 1 | 1187.8326 | Sq.M |  | 0
|  | Ground Floor | 1519.4547 | Sq.M |  | 0
|  | First Floor | 1428.84 | Sq.M |  | 0
19 |  | Providing and laying Cast in situ / Ready Mix cement concrete M-40 of trap / granite / quartzite /gneiss metal for R.C.C. slabs, landings and steps as per detailed designs and drawings including steel centering, form work, cover blocks, laying / pumping, compaction finishing the formed surfaces with cement mortar 1:3 of sufficient minimum thickness to give a smoot hand even surface or roughening if special finish is to be provided and curing etc. complete, (Excluding reinforcement and structural steel). with fully automatic microprocess or based PLC without SCADA enabled reversible Drum Type mixer/ concrete Batch mix plant (Pan mixer) etc. complete. With fine aggregate (Crushed sand VSI Grade)
| 5.33.2.4 | Second Floor | 148.51 | Cu.M |  | 0
|  | Third Floor | 147.95 | Cu.M |  | 0
|  | Fourth Floor | 147.95 | Cu.M |  | 0
| 5.33.2.4 + 5.38 | Fifth Floor | 147.95 | Cu.M |  | 0
|  | Sixth Floor | 154.94 | Cu.M |  | 0
|  | Seventh Floor | 150.66 | Cu.M |  | 0
|  | Eighth Floor | 150.66 | Cu.M |  | 0
|  | Top Terrace | 141.94 | Cu.M |  | 0
Formwork
| 5.9.3 | Second Floor | 1082.6379 | Sq.M |  | 0
|  | Third Floor | 1078.5555 | Sq.M |  | 0
|  | Fourth Floor | 1078.5555 | Sq.M |  | 0
|  | Fifth Floor | 1078.5555 | Sq.M |  | 0
|  | Sixth Floor | 1129.5126 | Sq.M |  | 0
|  | Seventh Floor | 1098.3114 | Sq.M |  | 0
|  | Eighth Floor | 1098.3114 | Sq.M |  | 0
|  | Top Terrace | 1034.7426 | Sq.M |  | 0
20 |  | Providing and laying Cast in situ / Ready Mix cement concrete in M-50 of trap / granite / quartzite / gneiss metal for R.C.C. pardi of required thickness including steel centering, form work, cover blocks, laying /pumping, compacting and roughening them if special finish is to be provided and curing complete. (Excluding reinforcement and structural steel). with fully automatic microprocessor based PLC without SCADA enabled reversible Drum Type mixer / concrete Batch mix plant (Pan mixer)etc.complete.With fine aggregate (Crushed sand VSI Grade)
| 5.33.1.5 | Up to Basement 2 | 340.87 | Cu.M |  | 0
|  | Basement 2 | 468.61 | Cu.M |  | 0
|  | Basement 1 | 243 | Cu.M |  | 0
| 5.33.2.5 | Ground Floor | 55.91 | Cu.M |  | 0
|  | First Floor | 55.91 | Cu.M |  | 0
Formwork
| 5.9.2 | Up to Basement 2 | 2948.5255 | Sq.M |  | 0
|  | Basement 2 | 4053.4765 | Sq.M |  | 0
|  | Basement 1 | 2101.95 | Sq.M |  | 0
|  | Ground Floor | 483.6215 | Sq.M |  | 0
|  | First Floor | 483.6215 | Sq.M |  | 0
21 |  | Providing and laying Cast in situ / Ready Mix cement concrete in M-40 of trap / granite / quartzite / gneiss metal for R.C.C. pardi of required thickness including steel centering, form work, cover blocks, laying /pumping, compacting and roughening them if special finish is to be provided and curing complete. (Excluding reinforcement and structural steel). with fully automatic microprocessor based PLC without SCADA enabled reversible Drum Type mixer / concrete Batch mix plant (Pan mixer)etc.complete.With fine aggregate (Crushed sand VSI Grade)
| 5.33.2.4 | Second Floor | 37.67 | Cu.M |  | 0
|  | Third Floor | 41.44 | Cu.M |  | 0
|  | Fourth Floor | 43.33 | Cu.M |  | 0
| 5.33.2.4 + 5.38 | Fifth Floor | 45.21 | Cu.M |  | 0
|  | Sixth Floor | 37.67 | Cu.M |  | 0
|  | Seventh Floor | 37.67 | Cu.M |  | 0
|  | Eighth Floor | 37.67 | Cu.M |  | 0
|  | Top Terrace | 37.67 | Cu.M |  | 0
Formwork
| 5.9.3 | Second Floor | 325.8455 | Sq.M |  | 0
|  | Third Floor | 358.456 | Sq.M |  | 0
|  | Fourth Floor | 374.8045 | Sq.M |  | 0
|  | Fifth Floor | 391.0665 | Sq.M |  | 0
|  | Sixth Floor | 325.8455 | Sq.M |  | 0
|  | Seventh Floor | 325.8455 | Sq.M |  | 0
|  | Eighth Floor | 325.8455 | Sq.M |  | 0
|  | Top Terrace | 325.8455 | Sq.M |  | 0
22 | 4.20.2.3 | Providing and laying Cast in situ/Ready Mix cement concrete in M-20 of trap/ granite/ quartzite/ gneiss metal for R.C.C.coping to plinth or parapet and sill of doors and windows moulded as per detailed drawings or chamfered as approved by the Engineer including centering, formwork, cover blocks, laying/pumping, compacting , curing , finishing and roughening them if special finish is to be provided and curing complete. (Excluding reinforcement and structural steel).with fully automatic micro processor based PLC with SCADA enabled reversible Drum Type mixer/ concrete Batch mix plant (Pan mixer) etc. complete. With natural sand/V.S.I. quality Artificial Sand | 1.67 | Cu.M |  | 0
23 | LS | Providing and fixing MS stripd twisted tang bars conforming to IS:15369 in the walls/floor/roof slab of the vault area in 2 rows as per direction of Bank's Engineer. The reinforcement shall be made from mild steel strip to form a doubl comb structure. The weight of single tanng bar shall be minimum 6 kg. The comb strip shall be twisted in cylindrica shape, forming fangs in all directions. The rates shall include for cutting, twisting and placing the same as per direction of Bank's Engineer. The flanges shall overlap and interlock each other and shall be distributed in walls that they defect incoming drill giving resistance to burgalry attemps made on the vault room. (Godrej / Gunnebo ) ) | 3155 | Nos |  | 0
24 | 5.22 | Providing and fixing in position TMT - FE - 500 bar reinforcement of various diameters for R.C.C. pile caps, footings, foundations, slabs, beams columns, canopies, staircase, newels, chajjas, lintels pardis, copings, fins, arches etc. as per detailed designs, drawings and schedules. including cutting, bending, hooking the bars, binding with wires or tack welding and supporting as required complete.
|  | Up to Basement 2 | 196.41 | MT |  | 0
|  | Basement 2 | 110.16 | MT |  | 0
|  | Basement 1 | 84.42 | MT |  | 0
|  | Ground Floor | 81.44 | MT |  | 0
|  | First Floor | 63.23 | MT |  | 0
|  | Second Floor | 41.78 | MT |  | 0
|  | Third Floor | 44.96 | MT |  | 0
|  | Fourth Floor | 45.5 | MT |  | 0
|  | Fifth Floor | 46.04 | MT |  | 0
|  | Sixth Floor | 42.04 | MT |  | 0
|  | Seventh Floor | 42.5 | MT |  | 0
|  | Eighth Floor | 42.5 | MT |  | 0
|  | Top Terrace | 39 | MT |  | 0
|  | Bd-G : Brick Work | 879.98
25 |  | Providing Autoclaved Aerated Concrete Block masonary (with minimum 40% fly ash content by weight) of conforming to IS:2185 (Part 3) - 1984 in extra fine jointing mortar of fixoblock of UltraTech or equivalent in superstructure including striking joints, raking out joints and scaffolding etc. Complete. (The test shall be carried out conforming to IS:6441 (Part I) - 1972)
| 6.47 | Basement 2 | 32.86 | Cu.M. |  | 0
|  | Basement 1 | 14.01 | Cu.M. |  | 0
|  | Ground Floor | 137.28 | Cu.M. |  | 0
|  | First Floor | 72 | Cu.M. |  | 0
|  | Second Floor | 50.29 | Cu.M. |  | 0
|  | Third Floor | 65.97 | Cu.M. |  | 0
|  | Fourth Floor | 70.53 | Cu.M. |  | 0
| 6.47 + 6.5 | Fifth Floor | 68.87 | Cu.M. |  | 0
|  | Sixth Floor | 98.03 | Cu.M. |  | 0 |  |  |  | #DIV/0!
|  | Seventh Floor | 97.27 | Cu.M. |  | 0
|  | Eighth Floor | 95.09 | Cu.M. |  | 0
|  | Top Terrace | 51.31 | Cu.M. |  | 0
26 |  | Providing Autoclaved Aerated Concrete Block masonary (with minimum 40% fly ash content by weight) of conforming to IS:2185 (Part 3) - 1984 in extra fine jointing mortar of fixoblock of UltraTech or equivalent in 150mm thick wall including striking joints, raking out joints and scaffolding etc. Complete. (The test shall be carried out conforming to IS:6441 (Part I) - 1972)
| 6.47 | Ground Floor | 109.67 | Sq.M. |  | 0
|  | First Floor | 138.05 | Sq.M. |  | 0 |  |  |  | 0
|  | Second Floor | 14.88 | Sq.M. |  | 0
|  | Third Floor | 128.11 | Sq.M. |  | 0
|  | Fourth Floor | 144.8 | Sq.M. |  | 0
| 6.47 + 6.5 | Fifth Floor | 125.26 | Sq.M. |  | 0
|  | Sixth Floor | 421.82 | Sq.M. |  | 0
|  | Seventh Floor | 443.87 | Sq.M. |  | 0
|  | Eighth Floor | 454.75 | Sq.M. |  | 0
|  | Top Terrace | 43.26 | Sq.M. |  | 0
Bd-J : Water Proofing
27 | 22.7.1 multiplied by 2.5 | Providing waterproofing in W.C. and bath including brick bat coba in all position including providing and laying 12mm bedding in cement mortor 1:3 on vergin concrete slab with waterproofing compound @ 1kg/per bag of cement laying brick bat coba of required thickness in cm 1:5 with waterproofing compound 1 kg/bag of cement grouting and finishing the top layer with 20mm thick brick bedding in cm mortor 1:3 with waterproofing compound 1 kg/per bag of cement and testing the treated portion for 48 hours by pond test and covering ten years' guarantee on requisite stamp paper including curing etc.complete.
|  | Ground Floor | 3.36 | Cu.M. |  | 0
|  | First Floor | 16.85 | Cu.M. |  | 0
|  | Second Floor | 16.85 | Cu.M. |  | 0
|  | Third Floor | 17.4 | Cu.M. |  | 0
|  | Fourth Floor | 16.85 | Cu.M. |  | 0
|  | Fifth Floor | 17.4 | Cu.M. |  | 0
|  | Sixth Floor | 9.59 | Cu.M. |  | 0
|  | Seventh Floor | 8.45 | Cu.M. |  | 0
|  | Eighth Floor | 9.71 | Cu.M. |  | 0
28 | 22.7.1 | Providing cement based water proofing treatment to terraces (Indian water proofing or alike) with brick bats laid in required slope to drain the water for any span after cleaning the base surface. Applying a coat of cement slurry admixed with approved water proofing compound and laying the brick bats on bottom layer in C.M.1:5 admixed with approved water proofing compound filling up to half depth of brick bats, curing this layer for 3 days, applying cement slurry over this layer joints of brick bats with C.M.1:3 admixed with approved water proofing compound and finally top finishing with average 20 mm. thick layers of same mortar added with jute fiber at 1 Kg per bag including finishing the surface smooth with cement slurry admixed with approved water proofing compound. Marking finished surface with false squares of 300mm x 300 mm. making the junctions at the parapet rounded and tapered top for required height, with drip mould at the junction of plaster and parapet and curing and covering 10 years Guarantee against leakproofness on Court fee stamp paper of Rs. 500/- including ponding test etc. complete.
|  | First Floor | 54.15 | Sq.M. |  | 0
|  | Second Floor | 1 | Sq.M. |  | 0
|  | Third Floor | 19.05 | Sq.M. |  | 0
|  | Fourth Floor | 7.85 | Sq.M. |  | 0
|  | Fifth Floor | 7.85 | Sq.M. |  | 0
|  | Sixth Floor | 62.35 | Sq.M. |  | 0
|  | Seventh Floor | 54.15 | Sq.M. |  | 0
|  | Eighth Floor | 54.2 | Sq.M. |  | 0
|  | Terrace Floor | 630.65 | Sq.M. |  | 0
29 | 13.9.2 +13.21 | Providing waterproof bedding for flooring of Bath and WC 25 mm thick in C.M. 1:3 including using approved waterproofing compound in specified proportion as per manufacturers specifications for per bag of cement including leveling, curing and covering 10 years guarantee on court fee stamp paper of Rs.500/ including ponding test etc. complete
|  | Ground Floor | 11.2 | Sq.M. |  | 0
|  | First Floor | 56.15 | Sq.M. |  | 0
|  | Second Floor | 1 | Sq.M. |  | 0
|  | Third Floor | 58 | Sq.M. |  | 0
|  | Fourth Floor | 56.15 | Sq.M. |  | 0
|  | Fifth Floor | 58 | Sq.M. |  | 0
|  | Sixth Floor | 31.95 | Sq.M. |  | 0
|  | Seventh Floor | 28.15 | Sq.M. |  | 0
|  | Eighth Floor | 32.35 | Sq.M. |  | 0
30 | 22.1.1 Derive 22.1.1(-)11.69 | Providing and fixing 20 to 25 mm thick rough shahabad box type waterproofing for basement or underground floor on a base of Cement concrete 1:3:6, including sub base of 2.50 centimeter thick Cement mortar 1:3 with conceal, secrete (RMW), Algae proof or other alike waterproofing liquids, raking of joints upto 35 mm depth, filling the joints with 6 mm size crushed metal, hand grouting with cement slurry, curing and cleaning, with 7 years guarantee on court fee stamp of Rs. 100/- with ponding test etc complete. (excluding Cement concrete 1:3:6 base concrete )
|  | Below Ground | 1055.01 | Sq.M. |  | 0
31 | 22.1.1 Derive 22.1.1(-)11.69 | Providing and fixing 20 to 25 mm thick rough shahabad box type waterproofing treatment to vertical outside faces of Reinforced Cement concrete walls of basement or underground floor including filling the gap of 25 mm between rough shahabad and R.C.C. walls with cement grout mixed with water proofing liquid Algae proof or other alike with one tile lift method, brushing the joints horizontally with cement slurry mixed with water proofing liquid for width 30 to 35 mm and sloping coping over topmost tile with cement mortar 1:3, butting the bottom most with Cement concrete 1:2:4 mixed with water proofing liquid, curing, with 7 years guarantee on court fee stamp of Rs.100/- with ponding test etc complete. (excluding Cement concrete 1:3:6 base concrete)
|  | Below Ground | 740.15 | Sq.M. |  | 0
|  | Basement 2 | 845.34 | Sq.M. |  | 0
|  | Basement 1 | 675.73 | Sq.M. |  | 0
32 | 13.9.2 +13.21 | Providing waterproof plaster in 20 mm thick in cement mortar 1:3 with neat finishing, floating using waterproofing compound at the rate of 1 Kilogram. per bag of cement of approved make and manufacturer and curing (and filling joints of Nahani trap and any outlet by properly) etc. complete. Car lift, Passenger & Fire lift internal side (Below Ground Floor) | 212 | Sq.M. |  | 0
33 | 22.23 | Providing and applying a base coat comprising of 1 Kg Polydee- MC and 1 Kg fresh cement after wetting the surface followed by drying the surface for 2 days, apply primer coat of TP-40 and after drying, applying Polydee-11 two component (mixing ratio 2 A : 1 B) ) Antibacterial food grade coating inside drinking water tank in two coats with time interval of minimum 8 hrs. covering 7 years guarantee on Court Fee Stamp Paper of Rs. 100/- etc. complete.
| 22.23.1 | Below Ground | 347.02 | Sq.M. |  | 0
|  | Above Terrace | 127.92 | Sq.M. |  | 0
Bd-L : Plastering and Pointing
34 | 13.5.1 | Providing sand faced plaster externally in cement mortar using approved screened sand, in all positions including base coat of 15 mm thick in cement mortar 1:4 using waterproofing compound at 1 kg per cement bag curing the same for not less than 2 days and keeping the surface of the base coat rough to receive the sand faced treatment 6 to 8 mm thick in cement mortar 1:4 finishing the surface by taking out grains and curing for fourteen days scaffolding etc.complete.
|  | Basement 2 | 894.31 | Sq.M. |  | 0
|  | Basement 1 | 657.08 | Sq.M. |  | 0
|  | Ground Floor | 999.56 | Sq.M. |  | 0
|  | First Floor | 577.32 | Sq.M. |  | 0
|  | Second Floor | 623.23 | Sq.M. |  | 0
|  | Third Floor | 478.42 | Sq.M. |  | 0
|  | Fourth Floor | 456.51 | Sq.M. |  | 0
|  | Fifth Floor | 499.59 | Sq.M. |  | 0
|  | Sixth Floor | 687.83 | Sq.M. |  | 0
|  | Seventh Floor | 706.92 | Sq.M. |  | 0
|  | Eighth Floor | 696.66 | Sq.M. |  | 0
|  | Terrace Floor | 605.52 | Sq.M. |  | 0
35 | 13.7.1 | Providing internal cement plaster 12mm thick in single coat in cement mortar 1:3 without neeru finish to oncrete or brick surfaces, in all position including scaffolding and curing etc. complete.
Internal Plaster
|  | Basement 2 | 543.43 | Sq.M. |  | 0
|  | Basement 1 | 341.45 | Sq.M. |  | 0
|  | Ground Floor | 1274.89 | Sq.M. |  | 0
|  | First Floor | 928.5 | Sq.M. |  | 0
|  | Second Floor | 187.08 | Sq.M. |  | 0
|  | Third Floor | 907.39 | Sq.M. |  | 0
|  | Fourth Floor | 1073.01 | Sq.M. |  | 0
|  | Fifth Floor | 1015.9 | Sq.M. |  | 0
|  | Sixth Floor | 1460.93 | Sq.M. |  | 0
|  | Seventh Floor | 1456.36 | Sq.M. |  | 0
|  | Eighth Floor | 1401.51 | Sq.M. |  | 0
|  | Top Terrace | 193.15 | Sq.M. |  | 0
36 | 13.78 | Providing and applying gypsum plaster ( with Gypsum material ) with finishing with gypsum material in 10 to 13 millimeter thickness to previously plastered surface / or on newly brick surface ( Excluding rough cast plaster ) in all position including preparing and Finishing the surface scaffolding etc.complete
|  | Ground Floor | 1274.89 | Sq.M. |  | 0
|  | First Floor | 928.5 | Sq.M. |  | 0
|  | Second Floor | 187.08 | Sq.M. |  | 0
|  | Third Floor | 907.39 | Sq.M. |  | 0
|  | Fourth Floor | 1073.01 | Sq.M. |  | 0
|  | Fifth Floor | 1015.9 | Sq.M. |  | 0
|  | Sixth Floor | 1460.93 | Sq.M. |  | 0
|  | Seventh Floor | 1456.36 | Sq.M. |  | 0
|  | Eighth Floor | 1401.51 | Sq.M. |  | 0
|  | Top Terrace | 34.7 | Sq.M. |  | 0
37 | 13.26 | Providing and applying Two coats of wall care Putty on plastered surface and Ceiling and Walls to prepare surface even and smooth of approved make, etc complete.
|  | Basement 2 | 660.14 | Sq.M. |  | 0
|  | Basement 1 | 440.71 | Sq.M. |  | 0
|  | Ground Floor | 1658.31 | Sq.M. |  | 0
|  | First Floor | 1232.79 | Sq.M. |  | 0
|  | Second Floor | 767.09 | Sq.M. |  | 0
|  | Third Floor | 1381.95 | Sq.M. |  | 0
|  | Fourth Floor | 1574.6 | Sq.M. |  | 0
|  | Fifth Floor | 1476.98 | Sq.M. |  | 0
|  | Sixth Floor | 1697.53 | Sq.M. |  | 0
|  | Seventh Floor | 1753.46 | Sq.M. |  | 0
|  | Eighth Floor | 1631.76 | Sq.M. |  | 0
|  | Top Terrace | 227.85 | Sq.M. |  | 0
Bd-M : Paving,Flooring and Dado
38.1 | 11.23.2 | Providing and laying machine cut, mirror polished Marble stone flooring,in required design (Simple geometrical, abstract etc.) and in patterns in combination with Italian marble stones of different colours, shades and finished surface texture etc., in linear portions of the building, all complete as per the architectural drawings, with 18 mm thick stone slab laid over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with white cement slurry @ 4.4 kg/sqm, including pointing with white cement slurry admixed with pigment to match the marble shade, including rubbing, curing and polishing etc. all complete as specified and as directed by the Engineer-in-Charge
|  | Basement 2 | 34.2 | Sq.M. |  | 0
|  | Basement 1 | 34.2 | Sq.M. |  | 0
|  | Ground Floor | 34.2 | Sq.M. |  | 0
|  | First Floor | 34.2 | Sq.M. |  | 0
|  | Second Floor | 34.2 | Sq.M. |  | 0
|  | Third Floor | 34.2 | Sq.M. |  | 0
|  | Fourth Floor | 34.2 | Sq.M. |  | 0
|  | Fifth Floor | 34.2 | Sq.M. |  | 0
|  | Sixth Floor | 34.2 | Sq.M. |  | 0
|  | Seventh Floor | 34.2 | Sq.M. |  | 0
|  | Eighth Floor | 34.2 | Sq.M. |  | 0
38.2 | 11.56.1 | Providing and laying in position flooring of telephone black / Amba White / Cat bary brown / Ruby red / Ocean Brown granite stone of approved shade and size 18 mm to 20 mm thick on bed 1:6 cement mortar including cement floats striking joints, pointing in C.M. 1:3 curing and cleaning etc. complete.
|  | Basement 2 | 44.41 | Sq.M. |  | 0
|  | Basement 1 | 30.12 | Sq.M. |  | 0
|  | Ground Floor | 30.03 | Sq.M. |  | 0
|  | First Floor | 30.12 | Sq.M. |  | 0
|  | Second Floor | 30.12 | Sq.M. |  | 0
|  | Third Floor | 30.12 | Sq.M. |  | 0
|  | Fourth Floor | 30.12 | Sq.M. |  | 0
|  | Fifth Floor | 30.12 | Sq.M. |  | 0
|  | Sixth Floor | 30.12 | Sq.M. |  | 0
|  | Seventh Floor | 30.12 | Sq.M. |  | 0
|  | Eighth Floor | 30.12 | Sq.M. |  | 0
39 | 11.56.1 | Providing and laying telephone black / Amba White / Cat bary brown / Ruby red / Ocean Brown granite stone of approved shade and size 18 mm to 20 mm thick for treads and risers of steps and staircases, with rounded nosing for the treads on a bed of 1:4 cement mortar including Treads including sandblasted, acid wash and three groves, cement float, filling joints with neat cement slurry, curing,polishing,uniform thickness for nosing and cleaning etc. complete.
|  | Basement 2 | 45.8 | Sq.M. |  | 0
|  | Basement 1 | 40.55 | Sq.M. |  | 0
|  | Ground Floor | 35.19 | Sq.M. |  | 0
|  | First Floor | 35.19 | Sq.M. |  | 0
|  | Second Floor | 35.19 | Sq.M. |  | 0
|  | Third Floor | 35.19 | Sq.M. |  | 0
|  | Fourth Floor | 35.19 | Sq.M. |  | 0
|  | Fifth Floor | 35.19 | Sq.M. |  | 0
|  | Sixth Floor | 35.19 | Sq.M. |  | 0
|  | Seventh Floor | 35.19 | Sq.M. |  | 0
|  | Eighth Floor | 35.19 | Sq.M. |  | 0
40 | 8.1.1.2 | Providing and fixing machine cut, mirror/ eggshell polished , Marble stone work for wall lining (Cladding work) including dado, skirting, risers of steps etc., in required design and pattern (if required with marble stone slab pieces of different shapes, sizes & texture but of even thickness) on 12 mm (average) thick cement mortar 1:3 (1 cement : 3 coarse sand) laid and jointed with white cement slurry @ 3.3 kg/sqm including pointing with white cement slurry admixed with pigment of matching shade,including rubbing, curing, polishing etc. all complete as per Architectural drawings, and as directed by the Engineer-in-Charge.
|  | Ground Floor | 15.24 | Sq.M. |  | 0
|  | First Floor | 15.24 | Sq.M. |  | 0
|  | Second Floor | 15.24 | Sq.M. |  | 0
|  | Third Floor | 15.24 | Sq.M. |  | 0
|  | Fourth Floor | 15.24 | Sq.M. |  | 0
|  | Fifth Floor | 15.24 | Sq.M. |  | 0
|  | Sixth Floor | 15.24 | Sq.M. |  | 0
|  | Seventh Floor | 15.24 | Sq.M. |  | 0
|  | Eighth Floor | 15.24 | Sq.M. |  | 0
41 | 11.41A.1.3 | Providing and laying vitrified mirror / glossy finish tiles decorative type having size 1200 mm X 600 mm of 9 to 10 mm thickness and confirming to IS. 15622- 2006 ( group Bla) of approved make, shade and pattern for flooring in required position laid on a bed of 1:4 cement mortar including neat cement float, filling joints, curing and clearing etc. complete. a) Flooring
|  | Basement 2 | 33.15 | Sq.M. |  | 0
|  | Basement 1 | 15.7 | Sq.M. |  | 0
|  | Ground Floor | 357.15 | Sq.M. |  | 0
|  | First Floor | 348.05 | Sq.M. |  | 0
|  | Second Floor | 348.05 | Sq.M. |  | 0
|  | Third Floor | 510.2 | Sq.M. |  | 0
|  | Fourth Floor | 519.55 | Sq.M. |  | 0
|  | Fifth Floor | 520.7 | Sq.M. |  | 0
|  | Sixth Floor | 407.49 | Sq.M. |  | 0
|  | Seventh Floor | 411.2 | Sq.M. |  | 0
|  | Eighth Floor | 364.95 | Sq.M. |  | 0 | 3836.19
42 | 11.41A.1.3 | Providing and laying vitrified mirror / glossy finish tiles having size 1200 mm X 600 mm of 9 to 10 mm thickness and confirming to IS. 15622-2006 ( group Bla) of approved make, shade and pattern for flooring in required position laid on a bed of 1:4 cement mortar including neat cement float, filling joints, curing and clearing etc. complete. b) Skirting
|  | Basement 2 | 3.23 | Sq.M. |  | 0
|  | Basement 1 | 1.5 | Sq.M. |  | 0
|  | Ground Floor | 30.11 | Sq.M. |  | 0
|  | First Floor | 15.73 | Sq.M. |  | 0
|  | Second Floor | 15.73 | Sq.M. |  | 0
|  | Third Floor | 19.33 | Sq.M. |  | 0
|  | Fourth Floor | 23.77 | Sq.M. |  | 0
|  | Fifth Floor | 20.02 | Sq.M. |  | 0
|  | Sixth Floor | 37.46 | Sq.M. |  | 0
|  | Seventh Floor | 38.15 | Sq.M. |  | 0
|  | Eighth Floor | 34.64 | Sq.M. |  | 0
43 | 11.41A.3.2 | Providing and laying vitrified rustic matt stone finish tiles having size 1200 mm X 600 mm of 9 to 10 mm thickness and confirming to IS. 15622-2006 (Group Bla) of approved make, shade and pattern for flooring in required position laid ?on a bed of 1:4 cement mortar including neat cement float, filling joints, curing and cleaning etc. complete. a) Flooring
Toilet Flooring
|  | Ground Floor | 5.4 | Sq.M. |  | 0
|  | First Floor | 23.5 | Sq.M. |  | 0
|  | Second Floor | 23.5 | Sq.M. |  | 0
|  | Third Floor | 14.25 | Sq.M. |  | 0
|  | Fourth Floor | 12.4 | Sq.M. |  | 0
|  | Fifth Floor | 14.25 | Sq.M. |  | 0
|  | Sixth Floor | 31.95 | Sq.M. |  | 0
|  | Seventh Floor | 28.15 | Sq.M. |  | 0
|  | Eighth Floor | 32.35 | Sq.M. |  | 0 | 185.75
44 | 8.31 | Providing and laying ceramic tiles having size 60 cm. x 60 cm. confirming to corresponding I.S. for dado and skirting in required position with readymade adhesive mortar of approved quality on plaster of 1:2 cement mortar including joint filling with white/ colour cement slurry cleaning curing etc. complete.
|  | Ground Floor | 57.54 | Sq.M. |  | 0
|  | First Floor | 181.36 | Sq.M. |  | 0
|  | Second Floor | 181.36 | Sq.M. |  | 0
|  | Third Floor | 130.52 | Sq.M. |  | 0
|  | Fourth Floor | 120.99 | Sq.M. |  | 0
|  | Fifth Floor | 130.52 | Sq.M. |  | 0
|  | Sixth Floor | 198.41 | Sq.M. |  | 0
|  | Seventh Floor | 177.04 | Sq.M. |  | 0
|  | Eighth Floor | 198.83 | Sq.M. |  | 0 | 1376.57
45 | Extra Item | Providing and laying Antiskid Ceramic tiles of approved quality of size 60 cm x 60 cm and confirming to IS 15622-2006 (Group-B IIA) for antiskid flooring in required position laid on a bed of 1:4 cement mortar including cement float, filling joint with cement slurry cleaning curing etc. complete a) Dry Balcony + Balcony + Terrace Flooring
|  | Basement 2 | 15 | Sq.M. |  | 0
|  | Basement 1 | 15 | Sq.M. |  | 0
|  | Ground Floor | 15 | Sq.M. |  | 0
|  | First Floor | 54.15 | Sq.M. |  | 0
|  | Second Floor | 15 | Sq.M. |  | 0
|  | Third Floor | 19.05 | Sq.M. |  | 0
|  | Fourth Floor | 7.85 | Sq.M. |  | 0
|  | Fifth Floor | 7.85 | Sq.M. |  | 0
|  | Sixth Floor | 66.35 | Sq.M. |  | 0
|  | Seventh Floor | 54.15 | Sq.M. |  | 0
|  | Eighth Floor | 54.2 | Sq.M. |  | 0 | 323.6 | 5722.11 | 858.3165 | 6580.4265 | 7896.5118
46 | 8.31 | Providing and laying ceramic tiles having size 60 cm. x 60 cm. confirming to corresponding I.S. for dado and skirting in required position with readymade adhesive mortar of approved quality on plaster of 1:2 cement mortar including joint filling with white/ colour cement slurry cleaning curing etc. complete. a) Balcony + Terrace Skirting
|  | Bd-P : Colour,white washing,distempering |  |  |  | 0
SUBMERSIBLE TRANSFER PUMP TOTAL AMOUNT
Civil
Plumbing

## Fire pump
EXTERNAL FIRE FIGHTING WORKS
EXTERNAL HYDRANT SYSTEM
Item No. |  | Particulars | Quantity | Unit | Rate (RS.) | Amount ( Rs. )
1 | 18.12.8 | Supplying and erecting G.I. pipe ‘C’ class ERW 75/80 mm dia with necessary fittings complete as per specification no. FF-PP. | 6 | Mtrs. | 919.1 | 5514.6
2 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 100 mm dia with necessary fittings complete as per specification no. FF-PP | 10 | Mtrs. | 1200 | 12000
3 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 150 mm dia with necessary fittings complete as per specification no. FF-PP | 180 | Mtrs. | 1800 | 324000
4 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 200 mm dia with necessary fittings complete as per specification no. FF-PP | 1 | Mtrs. | 2800 | 2800
5 |  | Providing coating of bitumen paint & 4mm thick wrapping for underground 200 mm ring main of fire fighting system. | 16 | Mtrs. | 250 | 4000
6 |  | Supplying and erecting brass orifice plate having 6 mm. thickness, 140 mm outer dia with required diameter of inner hole at every single outlet hydrant valve as per specification no. FF-FFA/OP | 2 | Nos. | 1650 | 3300
7 |  | Supplying and erecting brass orifice plate having 6 mm. thickness, 160 mm outer dia with required diameter of inner hole at every single outlet hydrant valve as per specification no. FF-FFA/OP | 2 | Nos. | 1650 | 3300
8 |  | Supplying and erecting 100 mm dia. cast iron double flange butterfly valve of size complete with PN16 pressure rating, as per specification no. FF-VL/BFV | 2 | Nos. | 6000 | 12000
9 |  | Supplying and erecting 150 mm dia. cast iron double flange butterfly valve of size complete with PN16 pressure rating, as per specification no. FF-VL/BFV | 3 | Nos. | 9000 | 27000
10 |  | Supplying and erecting gun metal single outlet hydrant valve fitted with necessary accessories complete as per specification no. FF-VL/HV | 3 | Nos. | 9500 | 28500
11 | 9.1 | Supplying gun metal double outlet hydrant valve fitted with necessary accessories complete as per specification no. FF-VL/HV | 3 | Nos. | 7494 | 22482
12 | 17.2 | Supplying and installing wall mounting swinging hose reel drum fitted with 19mm dia. 30m long high pressure polypropylene (Polyhose) along with necessary accessories complete as per specification no. FF-FFA/HV | 6 | Nos. | 8413 | 50478
13 |  | Supplying and erecting 63mm dia, reinforced rubber lined (R.R.L.) hose pipe, 15m in length, fitted with necessary accessories complete as per specification no. FF-FFA/RRL | 6 | Nos. | 4434 | 26604
14 |  | Supplying and erecting gun metal branch pipe of 63 mm dia fitted with 20 mm dia detachable hexagonal nozzle complete as per specification no. FF | 6 | Nos. | 5188 | 31128
15 |  | Excavating hard murum / stone metal road by chiselling for preparing pit for poles stay or earth plates or for laying cables, pipes & clearing the site by removing debris & making the site as required complete. | 12 | Cu.M. | 286 | 3432
|  | FIRE BRIGADE BREACHING AND SIAMESE INLET CONNECTIONS |  |  |  | 0
16 | 19.2 | Supplying, Installation,testing & commissioning of 4-Way inlet for external and tank of 150 mm dia.,G.I. 'C' class pipe, having 4 nos of 63 mm SS instantaneous inlet, 1 no. 150mm with spring type NRV, with all necessary accessories to make the system complete. | 1 | Set | 16586.4 | 16586.4
17 |  | Supplying, Installation,testing & commissioning of 3-Way inlet for wet riser. Header of 150 mm dia.,G.I. 'C' class pipe, having 2 nos of 63 mm SS instantaneous inlet, 1 no. 150mm with spring type NRV. | 1 | Nos. | 11162.4 | 11162.4
18 |  | Supplying, Installation,testing & commissioning of fire water drawoff connection of 150mm dia GI "C" class pipe, from UGR to upper basement with foot valve & with all necessary accessories to make the system complete. Piping will be measured separately | 1 | Set | 5000 | 5000
19 |  | Supplying and erecting 150 mm dia. cast iron double flange butterfly valve of size complete with PN16 pressure rating, as per specification no. FF-VL/BFV SSR Item No. 13-7-21 | 3 | Nos. | 8699 | 26097
|  | FIRE PUMPS ACCESSORIES (PIPING & VALVES) |  |  |  | 0
20 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 25 mm dia with necessary fittings complete as per specification no. FF-PP | 6 | Mtrs. | 417.95 | 2507.7
21 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 50 mm dia with necessary fittings complete as per specification no. FF-PP | 12 | Mtrs. | 654.2 | 7850.4
22 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 75/80 mm dia with necessary fittings complete as per specification no. FF-PP | 6 | Mtrs. | 919.1 | 5514.6
23 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 150 mm dia with necessary fittings complete as per specification no. FF-PP | 12 | Mtrs. | 1600 | 19200
24 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 200 mm dia with necessary fittings complete as per specification no. FF-PP | 12 | Mtrs. | 2800 | 33600
25 |  | Supplying and erecting 150 mm dia. cast iron double flange butterfly valve of size complete with PN16 pressure rating, as per specification no. FF-VL/BFV | 4 | Nos. | 8699 | 34796
26 |  | Supplying and erecting 75/80 mm dia Cast Iron end line strainer of Y-type flanged end pattern, PN16 pressure rating, SS screen, end connection with Flanged / Screwed / Socket Weld / Butt Weld End etc with standard OAR (open area Ratio) for positive suction complete as per specification no. FF-VL/ELS | 1 | Nos. | 4573 | 4573
27 |  | Supplying and erecting 100 mm dia Cast Iron end line strainer of Y-type flanged end pattern, PN16 pressure rating, SS screen, end connection with Flanged / Screwed / Socket Weld / Butt Weld End etc with standard OAR (open area Ratio) for positive suction complete as per specification no. FF-VL/ELS | 3 | Nos. | 6450 | 19350
28 |  | Supplying and erecting 150 mm dia Cast Iron end line strainer of Y-type flanged end pattern, PN16 pressure rating, SS screen, end connection with Flanged / Screwed / Socket Weld / Butt Weld End etc with standard OAR (open area Ratio) for positive suction complete as per specification no. FF-VL/ELS | 1 | Nos. | 10659 | 10659
29 |  | Supplying and erecting 200 mm dia Cast Iron end line strainer of Y-type flanged end pattern, PN16 pressure rating, screen of SS end connection with Flanged / Screwed / Socket Weld / Butt Weld End etc with standard OAR (open area Ratio) for positive suction complete as per specification no. FF-VL/ELS | 1 | Nos. | 22052 | 22052
30 |  | Supplying and erecting 75/80 mm dia cast iron double flange NRV complete with PN16 pressure rating, as per specification no. FF-VL/NRV | 1 | Nos. | 7539 | 7539
31 |  | Supplying and erecting 100 mm dia cast iron double flange NRV complete with PN16 pressure rating, as per specification no. FF-VL/NRV | 1 | Nos. | 10836 | 10836
32 |  | Supplying and erecting 150 mm dia cast iron double flange NRV complete with PN16 pressure rating, as per specification no. FF-VL/NRV | 3 | Nos. | 17577 | 52731
33 |  | Supplying and erecting 100 mm dia. pressure gauge , 0-300 PSI or 0-14 kg per cm square fitted with 12/15 mm dia. pad cock valve, erected with provided G.I. pipe, elbow etc. complete as per specification no. FF-FFA/PG. | 3 | Nos. | 800 | 2400
34 |  | Supplying, Installation,testing & commissioning of fire sprinkler annunciation panel of 55 windows with required controls & logic, Power & control internal wiring. | 1 | Nos. | 175000 | 175000
35 |  | Supplying and erecting 12/15 mm dia pressure switch with provided isolation valve, G.I. nipple, elbow, etc complete as per specification no. FF-FFA/PS | 3 | Nos. | 1508 | 4524
36 |  | Supplying, Installation,testing & commissioning of MS pressure vessel of suitable capacity & PN 25 with required safety valves and all accessories to make the system complete.. | 1 | Nos. | 18009 | 18009
|  | FIRE PUMPS & EQUIPMENTS |  |  |  | 0
37 | 18.1.1 E&M | Supplying, installation, testing and commissioning of main fire pump (MFP/DP) suitable for water discharge of 2280 to 2850 LPM at 90 to 60 m head driven by 76 HP or suitable HP capacity diesel engine at required working speed suitable for manual/automatic operation and consisting of following : (a) Horizontal type, single stage, centrifugal casing pump of cast iron body & bronze impeller with stainless steel shaft(SS410 grade), mechanical seal conforming to IS 1520. (b) Water cooled with radiator, diesel engine conforming to relevant IS standard complete with auto starting mechanism, 12/24 volts DC electric starting equipment with battery of required AH capacity with necessary charger suitable to work on 230v, 50Hz AC supply, diesel tank of minimum 150ltr capacity with first filling of diesel up to 100% level with necessary piping with valves up to engine ,exhaust pipe extended up to 10 m outside pump house duly insulated with 50 mm thick glass wool with 1.0 mm thick aluminium sheet cladding, residential silencer, instruments and | 1 | Set | 452519 | 452519
|  | protection as per standard specification, stop solenoid for auto stop in the event of fault with audio indications etc. as required. (c) M.S. fabricated common base plate, coupling, coupling guard, foundation bolts etc. as required. (d) Erected on provided suitable size cement concrete foundation duly plastered with anti vibration pads with perfect aligning, proper levelling complete pump set with engine assembly and accessories duly painted with two coats of synthetic enamel paint of fire red colour over a coat of primer (ISC code 536 as per IS 2932 of 2003) complete, as per specification no. FF-MFP/SSC/DP |  |  |  | 0
38 | 18.1.1 E&M | Supplying, installation, testing and commissioning of main fire pump (MFP /EP) suitable for water discharge of 2280 to 2850LPM at 80 to 60 m head driven by electric motor 415 volts, 3 phase 50 Hz, AC supply of 45kW or of suitable kW capacity for manual/automatic operation and consisting of following : (a) Horizontal type, single stage, centrifugal/split casing pump of cast iron body & bronze impeller with stainless steel shaft(SS410 grade), mechanical seal conforming to IS 1520. (b) Squirrel cage induction motor, TEFC, synchronous speed 3000 RPM, suitable for operation with IP 55 protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS-325. (c) M.S. fabricated common base plate, coupling, coupling guard, foundation bolts etc. as required | 1 | Set | 452519 | 452519
|  | (d) Erected on provided suitable size cement concrete foundation duly plastered with anti vibration pads with perfect aligning, proper levelling complete pump set with accessories duly painted with two coats of synthetic enamel paint of fire red colour over a coat of primer (ISC code 536 as per IS 2932 of 2003) complete, as per specification no. FF-MFP/SSC/EP |  |  |  | 0
39 | 18.1.1 E&M | Supplying, installation, testing and commissioning of main fire pump (MFP /EP) suitable for water discharge of 2280 to 2850 LPM at 90 to 70 m head driven by electric motor 415 volts, 3 phase 50 Hz, AC supply of 55kW or of suitable kW capacity for manual/automatic operation and consisting of following : (a) Horizontal type, single stage, centrifugal/split casing pump of cast iron body & bronze impeller with stainless steel shaft (SS410 grade), mechanical seal conforming to IS 1520. (b) Squirrel cage induction motor, TEFC, synchronous speed 3000 RPM, suitable for operation on with IP 55 protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS-325. (c) M.S. fabricated common base plate, coupling, coupling guard, foundation bolts etc. as required. (d) Erected on provided suitable size cement concrete foundation duly plastered with anti vibration pads with perfect aligning, proper levelling complete pump set with accessories duly painted with two coats of synthetic enamel paint of fire red colour over a coat of primer (ISC code 536 as per IS 2932 of 2003) complete, as per specification no. FF-MFP/SSC/EP | 1 | Set | 452519 | 452519
40 | 18.1.1 E&M | For standby main electric motor driven fire hydrant/sprinkler system pump (MFP- 1 standby), add as follows in the basic cost of Item no 13-5-1 towards required switchgears and motor starter along with necessary accessories and updation of control logic with interlocking for operation of pumps MFP=(1working+1standby, alternate run per start in auto mode) JP = (1working+1standby, alternate run per start in auto mode) for main & jockey fire pumps | 1 | Set | 254296 | 254296
|  | For addition of standby main diesel engine driven fire pump (1 standby),add as follows in the basic cost of Item no 13-5-1 towards required 12/24 vbattery charger and diesel engine starter along with necessary accessories, indicators etc. with necessary interlocking and updation of control logic with interlocking for operation of pumps MFP for main (1working+1standby mode)& jockey fire pumps (1working+1standby, alternate run per start in auto mode) ,add Rs.......The control for diesel engine comprises of automatic/manual selector switch & 3attempts starting device, timers and relays as required, push buttons, start/stop in manual mode indicating lamp for high/ low Lub. oil pressure, high water temp and engine on indication battery charger suitable for 12V/24 V DC with boost and trickle selector switch, 0-30 V DC voltmeter, and 0-20 A DC ammeter with all standard relays and accessories required for automatic operation of diesel engine with interlocking for operation of main fire pumps |  |  |  | 0
41 |  | Supplying, installation, testing and commissioning of booster fire pump [BP] suitable for water discharge of 900 LPM at 35 m head driven by electric motor 415 volts, 3 phase 50 Hz, AC supply of 7.5 kW or of suitable kW capacity for manual/automatic operation and consisting of following : (a) Horizontal/vertical type, single/multi stage, centrifugal casing pump of cast iron body & bronze/CI impeller with stainless steel shaft (SS410 grade), mechanical seal conforming to IS 1520. (b) Squirrel cage induction motor, TEFC, synchronous speed 3000 RPM, suitable for operation on with IP 55 protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS 325. (c) M.S. fabricated common base plate, coupling, coupling guard, foundation bolts etc. as required. (d)Erected on provided suitable size cement concrete foundation duly plastered with anti vibration pads with perfect aligning, proper levelling complete pump setwith accessories duly painted with two coats of synthetic enamel paint of fire red colour over a coat of primer (ISC code 536 as per IS 2932 of 2003) complete, as per specification no. FF-MFP/BP | 2 | Set | 72000 | 144000
42 |  | Supplying, installation, testing and commissioning of jockey fire pump (JP) suitable for water discharge of 180 to 240 LPM at 90 to 70 m head driven by electric motor 415 volts, 3 phase 50 Hz, AC supply of 9.3 kW or of suitable kW capacity for manual/automatic operation and consisting of following : (a) Horizontal/vertical type, multi stage, centrifugal casing pump of cast iron body & bronze impeller with stainless steel shaft(SS410 grade), mechanical seal conforming to IS 1520. (b) Squirrel cage induction motor, TEFC, synchronous speed 3000 RPM, suitable for operation with IP 55 protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS-325.(c) M.S. fabricated common base plate, coupling, coupling guard, foundation bolts etc. as required. (d) Erected on provided suitable size cement concrete foundation duly plastered with anti vibration pads with perfect aligning, proper levelling complete pump set with accessories duly painted with two coats of synthetic enamel paint of fire red colour over a coat of primer (ISC code 536 as per IS 2932 of 2003)complete, as per specification no. FF-MFP/JP | 1 | Nos | 245730 | 245730
| INTERNAL FIRE FIGHTING WORKS |  |  |  |  | 0
|  | INTERNAL HYDRANT SYSTEM |  |  |  | 0
43 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 75/80 mm dia with necessary fittings complete as per specification no. FF-PP. | 8 | Rmt | 919 | 7352
44 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 100 mm dia with necessary fittings complete as per specification no. FF-PP | 12 | Rmt | 1200 | 14400
45 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 150 mm dia with necessary fittings complete as per specification no. FF-PP | 40 | Rmt | 1800 | 72000
46 |  | Supplying and erecting 100 mm dia. cast iron double flange butterfly valve of size complete with PN16 pressure rating, as per specification no. FF-VL/BFV | 1 | No | 7494 | 7494
47 |  | Supplying and erecting 150 mm dia. cast iron double flange butterfly valve of size complete with PN16 pressure rating, as per specification no. FF-VL/BFV | 2 | No | 11162 | 22324
48 |  | Supplying and erecting 150 mm dia cast iron double flange NRV complete with PN16 pressure rating, as per specification no. FF-VL/NRV | 2 | No | 17577 | 35154
49 |  | Supply and installation of S.S landing valve with PN 16 pressure rating, oblique type single outlet confirming to IS 5290 completes with hose coupling adaptor 63 mm size instantaneous spring lock arrangement and PVC blank cap with ISI mark, provided with necessary nuts, bolts, gaskets etc.complete . | 10 | No | 1291 | 12910
50 |  | Supply and installation of first aid fire hose of braided rubber suitably reinforced of approved make 20mm size near standard length with 10mm tapering branch nozzle in SS, male & female coupling with cut off valve attachment. Hose to be swinging type well mounted drum & recessing into hose cabinet to suit location including fixing with lead anchor fasteners & bolts etc. complete. | 10 | No | 5188 | 51880
51 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 25 mm dia with necessary fittings complete as per specification no. FF-PP. | 10 | Rmt | 200 | 2000
52 |  | Supplying and erecting 63mm dia, reinforced rubber lined (R.R.L.) hose pipe, 15m in length, fitted with necessary accessories complete as per specification no. FF-FFA/RRL. | 10 | No | 5188 | 51880
53 |  | Supplying and erecting 20/25mm dia gun metal air release cock, with necessary G.I. coupling to be fitted on top of air vessel or on wet riser complete as per specification no. FF-FFA/ARV | 1 | No | 2000 | 2000
54 |  | Supplying and installation of M.S. Fabricated bracket of required size in structural steel with all necessary welding & fixing the same & grouting in wall / RCC wall using dash fasteners of required size with clamping the pipe with `U' clamp with nut & bolts with giving one coat of red oxide paint & 2-coat of enamel paint of bracket etc. complete. ( These supports are considered only at vertical places, like valves, extra bends etc.& for all floors) | 120 | Kg | 140 | 16800
55 |  | Supplying and erecting 100 mm dia. pressure gauge , 0-300 PSI or 0-14 kg per cm square fitted with 12/15 mm dia. pad cock valve, erected with provided G.I. pipe, elbow etc. complete as per specification no. FF-FFA/PG. | 8 | Nos | 1000 | 8000
57 |  | S Supplying and erecting 100 mm dia Cast Iron end line strainer of Y-type flanged end pattern, PN16 pressure rating, SS screen, end connection with Flanged / Screwed / Socket Weld / Butt Weld End etc with standard OAR (open area Ratio) for positive suction complete as per specification no. FF-VL/ELS. | 1 | Nos | 15000 | 15000
SEC II |  | FIRE SPRINKLER SYSTEM |  |  |  | 0
15 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 25 mm dia with necessary fittings complete as per specification no. FF-PP | 1460 | Rmt | 200 | 292000
16 |  | 32mm dia. | 340 | Rmt | 450 | 153000
17 |  | 40mm dia. | 36 | Rmt | 650 | 23400
18 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 50 mm dia with necessary fittings complete as per specification no. FF-PP | 40 | Rmt | 750 | 30000
19 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 65 mm dia with necessary fittings complete as per specification no. FF-PP | 10 | Rmt | 850 | 8500
20 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 75/80 mm dia with necessary fittings complete as per specification no. FF-PP. | 320 | Rmt | 920 | 294400
21 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 100 mm dia with necessary fittings complete as per specification no. FF-PP | 40 | Rmt | 1200 | 48000
22 |  | Supplying and erecting G.I. pipe ‘C’ class ERW 150 mm dia with necessary fittings complete as per specification no. FF-PP. | 40 | Rmt | 1800 | 72000
23 |  | Supplying and erecting 100 mm dia. cast iron double flange butterfly valve of size complete with PN16 pressure rating, as per specification no. FF-VL/BFV | 8 | Nos | 9000 | 72000
24 |  | Supplying and erecting 150 mm dia. cast iron double flange butterfly valve of size complete with PN16 pressure rating, as per specification no. FF-VL/BFV | 1 | Nos | 12000 | 12000
25 |  | Supplying, Installation,testing & commissioning of CP Brass,15mm inlet spray pattern, standard response pendant type sprinkler heads (ordinary hazard) with quartzoid bulb with temp rating of 68 deg. C. K value of sprinkler shall be 80, Sprinkler head shall be | 560 | Nos | 600 | 336000
26 |  | Supplying, Installation,testing & commissioning of CP Brass,15mm inlet spray pattern, standard response side wall type sprinkler heads (ordinary hazard) with quartzoid bulb with temp rating of 68 deg. C. K value of sprinkler shall be 80, Sprinkler head shall be | 36 | Nos | 750 | 27000
27 |  | Supplying and erecting 20/25mm dia gun metal air release cock, with necessary G.I. coupling to be fitted on top of air vessel or on wet riser complete as per specification no. FF-FFA/ARV | 1 | Nos | 2000 | 2000
28 |  | Supplying, Installation,testing & commissioning of approved make water flow switches ( Vane type ) including accessories suitable for up to 150mm dia. pipe as required with potential free contact 2 NO & NC contact. operating at 24-V at MCP (Main Console Panel). The flow switch will be UL approved | 2 | Nos | 17740 | 35480
29 |  | Supply and installation of Flexible hose pipe of 25mm dia with both end socket for fixing the sprinkler to ranger.Consider length of flexible piece as per below. This product has to be FM and UL approved. Flexible connectors should be supported with separate expansion bolts & not on the False ceiling frame work.The pressure carrying capacity of hose shall be 12 bar. The supporting arrangement to get approved from Ceiling Vendor prior to execution. |  |  |  | 0
|  | 1200mm Length | 560 | Nos | 1633 | 914480
30 |  | Supplying, Installation,testing & commissioning of Rosette plate , with all necessary accessories to make the system complete. | 560 | Nos | 207 | 115920
31 |  | Supplying and erecting 100 mm dia. pressure gauge , 0-300 PSI or 0-14 kg per cm square fitted with 12/15 mm dia. pad cock valve, erected with provided G.I. pipe, elbow etc. complete as per specification no. FF-FFA/PG. | 1 | Nos | 600 | 600
FIRE EXTINGUISHERS
32 |  | Supply and installation of portable fire extinguishers (A,B,C Type powder) with all accessories as per manufacture's specification., IS : 15683:2006 with wall mounted Bracket.
a) |  | 9 Kg Capacity | 24 | Nos. | 2500 | 60000
b) |  | 6 Kg Capacity | 16 | Nos. | 2200 | 35200
33 |  | Supplying & erecting Carbon Dioxide (CO2) fire extinguisher of 4.5 kg. capacity cartridge type conform to IS 2878 /15683 complete erected with necessary clamp made from 50 x 6 mm. M. S. flat with nut & bolts routed in wall complete. | 6 | Nos. | 3500 | 21000
|  | FIRE FIGHTING TOTAL AMOUNT |  |  |  | 5920283.1
INTERNAL ELECTRICAL WORK
1 |  | Standard Factory Built MCB Distribution Boards of Double Door complete with all end terminations with copper Lugs and provide Distribution schematic inside DB door and MCB of 10kA breaking capacity with 'C' characteristics etc.
1.1 |  | Supplying and erecting single pole and neutral distribution board (SPNDB), with 2 ways for incoming and 10 ways (10 poles) for outgoing SP MCBs, with door, 1.2mm thickness surface / flush mounted, IP 43 Protection on iron / GI frame as per specification no. SW-SWR/MCBDB | 11 | Nos.
|  | Incoming :- Supplying, erecting & marking FPMCB 40A to 63A, with rated short - circuit breaking capacity (Icn) 10kA in provided distribution board as per specification no. SW-SWR/MCB | 11 | Nos.
|  | Supplying, fixing and commissioning 2 pole, RCBO 6/10/16/20/25A, with overcurrent, rated short-circuit breaking capacity (10 kA) and earth leakage protection, with 30/100/300 mA sensitivity and short circuit and earth leakage trip indication as per specification no SW-RCCB/RCBO | 11 | Nos.
|  | Outgoing :- Supplying, erecting & marking SPMCB 6A to 32A, B-series with rated short - circuit breaking capacity (Icn) 10kA in provided distribution board as per specification no. SW-SWR/MCB | 330 | Nos.
1.2 |  | Supplying & erecting triple pole and neutral distribution board (TPNDB), SP/TP MCBs total 12 ways /36 poles, with door, 1.2mm thickness surface/flush mounted, IP 43 Protection on iron/GI frame (vertical busbar type) as per specification no. SW-SWR/MCBDB | 5 | Nos.
|  | Incoming :- Supplying, erecting & marking FPMCB 40A to 63A, with rated short - circuit breaking capacity (Icn) 10kA in provided distribution board as per specification no. SW-SWR/MCB | 5 | Nos.
|  | Supplying, fixing and commissioning 2 pole, RCBO 6/10/16/20/25A, with overcurrent, rated short-circuit breaking capacity (10 kA) and earth leakage protection, with 30/100/300 mA sensitivity and short circuit and earth leakage trip indication as per specification no SW-RCCB/RCBO | 5 | Nos.
|  | Outgoing :- Supplying, erecting & marking SPMCB 6A to 32A, B-series with rated short - circuit breaking capacity (Icn) 10kA in provided distribution board as per specification no. SW-SWR/MCB | 180 | Nos.
POINT WIRING
2 |  | Point wiring for light / ceiling fan / 5A/15A/5+15 socket outlet / 15A outlet for exhaust fan / TPN MCB, A/C outlet point/TV Point,. With 1.1 KV grade FRLS PVC insulated multithreaded copper conductor wires, in 25/32 mm dia PVC, with all accessories, exposed in slab / wall or on G.I. spacers fixed with no. 10 nettle fold wood screws with nylon plug complete with all conduit accessories g.i. saddles, MS switch boxes, factory built suitable for modular type switch accessories including 1.00 / 1.5 sq.mm PVC insulated copper earth continuity conductor, switches, sockets etc., / backelite (straight / angular) lamp holders, 3 plate ceiling rose / 3 core / twin flexible copper chords, connectors, painting etc. as per specification & drawings. Note :- Connections shall be done with crimped type tinned copper lugs and washers, 25 /32 mm dia PVC, HMS category with ISI mark , All switches and sockets shall be Modular Type, All sample boxes with accessories / fixtures shall be got approved from Consultants / Architects.
2.1 |  | Point wiring for light/bell concealed type in min 20 mm FRLS grade HMS PVC conduit with 1.5 sq.mm. (2+1E) FRLSH grade copper wires, modular type switch, earthing and required accessories as per specification No: WG- PW/CW | 497 | Nos.
2.2 |  | Secondary point wiring for additional light/ bell point in PVC trunking (casing-capping) with 1.5 sq.mm (2+1E) FRLSH grade copper wire with required accessories as per specification No: WG-PW/SW | 353 | Nos.
2.3 |  | Point wiring for ceiling fan concealed type in min 20 mm FRLS grade HMS PVC conduit with 1.5 sq.mm. (2+1E) FRLSH grade copper wires, modular type switch, earthing and required accessories as per specification No: WG- PW/CW | 1100 | Nos.
2.4 |  | Supplying and erecting modular type 3 pin 6 / 16A multi socket with safety shutter, duly erected on provided plate and box with wiring connections complete. | 718 | Nos.
2.5 |  | Supplying and erecting modular type switch 6A / 10A duly erected on provided plate and box with wiring connections complete. | 157 | Nos.
2.6 |  | Supplying and erecting modular type switch 16A duly erected on provided plate and box with wiring connections complete. | 247 | Nos.
2.7 |  | 63AFP, 10kA, MCB with MS Enclosure. (for UPS) | 36 | Nos.
2.8 |  | 63AFP, 10kA, MCB with IP65 Enclosure. | 26 | Nos.
2.9 |  | Supplying and erecting modular pop up Box 8 module erected with provided AV/ HDMI , RJ 45,6 A electrical sockets and switch on provided table. | 10 | Nos
2.1 |  | Supplying and erecting HMS PVC conduit FRLS grade 25 mm dia. with PVC accessories on wall /ceiling as per specification No: WG-MA/CON. | 500 | Mtr.
2.11 |  | Supplying and erecting HMS PVC conduit FRLS grade 32 mm dia. with PVC accessories on wall / ceiling as per specification No: WG-MA/CON. | 155 | Mtr.
2.12 |  | Supply and Installation of TV Outlet with inner and outer plate without wiring. | 51 | Nos.
2.13 |  | Supplying & erecting co-axial copper cable low voltage grade tri-shielded RG-6 as per specification No. WG-TW | 1305 | Mtr.
2.14 |  | Supply and Installation of Telephone Outlet with inner and outer plate without wiring. | 116 | Nos.
2.15 |  | Tel. Wires 2 pair Wires complete with 25 mm dia P.V.C. Pipe. | 2720 | Mtr.
2.16 |  | T.V. Splitter Box 4 way along with suitable MS Box in individual Electrical shaft / duct. | 1 | Nos.
2.17 |  | T.V. Splitter Box 6 way along with suitable MS Box in individual Electrical shaft / duct. | 1 | Nos.
2.18 |  | Supply, Installation of Crone Box, for min. 100Pair Telephone, including Ferrule numbering & Termination for Telephone System with Poweder coated MS box with Name Plate. | 1 | Nos.
2.19 |  | Supply, Installation of Crone Box, for min. 50Pair Telephone, including Ferrule numbering & Termination for Telephone System with Poweder coated MS box with Name Plate. | 1 | Nos.
2.2 |  | Supply, Installation of Crone Box, for min. 20Pair Telephone, including Ferrule numbering & Termination for Telephone System with Poweder coated MS box with Name Plate. | 1 | Nos.
2.21 |  | 100 Pair jelly filled armoured Telephone cable (MDF to Meter room-02) | 10 | Mtr.
2.22 |  | 50 Pair jelly filled armoured Telephone cable (MDF to Meter room-01) | 10 | Mtr.
2.23 |  | 20 Pair jelly filled armoured Telephone cable (Meter room to Crone box on each floor) | 10 | Mtr.
C |  | RACEWAYS & WIRING
3 |  | Supply and laying of Heavy gauge factory built Raceways / Conduits (for under floor trenches) on existing flooring. The raceways / conduits shall be fixed to the flooring with clamps for finished levels as per site conditions or through partitions with all accessories, bends, Tee joints, pull wire etc. but excluding the floor mounted junction boxes which shall be paid separately. The metal/PVC conduits/Raceways shall be earth with copper earthing clips at suitable intervals the distance between the data conduits & power conduits shall be maintained at least 6" apart.
3.1 |  | 100 x 38 mm Aluminium raceways, 2 mm thick. | 750 | Mtr.
4 |  | Supplying and laying of PVC insulated copper conductors as follows, through already laid raceway/PVC Conduit for computer /raw power.
4.1 |  | Supplying and erecting PVC insulated PVC round sheathed 2.5 sq.mm (50 no. x0.25 mm dia.) 3 core flexible multi stranded copper Industrial cable for voltage grade up to 1.1 kV | 4900 | Mtr.
D |  | Cable Trays
5 |  | Supplying and fixing 4 way GI. junction boxes with knock-outs on all sides suitable for Raceways/conduits. The knock out shall be removed at site as per requirements. The junction boxes shall be laid in trenches for Raceways/conduits. The top cover shall be fixed with counter sunk screws. (For floor trenches).
5.1 |  | 600x600x50mm | 80 | Mtr.
5.2 |  | 450x450x50mm | 60 | Mtr.
5.3 |  | Supplying and erecting iron work, sheet metal work consisting of CRCA sheets, various sections of iron, plates, chequered plates, rods, bars, MS pipes, etc. for panel board or any other purpose with bending, cutting, drilling and welding complete erected at the position with necessary materials duly painted with one coat of red oxide and two coats of enamel paint to match the switchgears or as per directions by the authority. | 3000 | KG
6 |  | Supply and installation of 2mm Thk. Pregalvanised Perforated type Cable Trays of given various sizes including horizontal and vertical bends, reducers, tees, cross members and other accessories as required and duly suspended from the ceiling / floor with MS Angle/GI Threaded rod or with perforated Z section on wall with necessary Hardware & accessories.
6.1 |  | JUNCTION BOX 150mm | 81 | Nos
6.2 |  | JUNCTION BOX 250mm | 10 | Nos
E |  | UPS SYSTEMS
1 |  | UPS - Supply, Installation, Testing & commissiong of 3 phase IN & 3 phase Out UPS
a |  | Supplying, erecting, testing and commissioning of 20kVA capacity online pure sine wave, with backup time of hrs. PWM & IGBT based UPS with 0.9 to unity output pf, 3 phase input and 3 phase output complete with all protections as per specification no. AP-UPS | 3 | Nos
b |  | Supplying and erecting 12V/150Ah tubular battery with battery terminal wirduly charged with 36 months warranty complete. | 3 | Nos
UPS I/P DB
1.1 |  | Supplying & erecting triple pole and neutral distribution board (TPNDB), SP/TP MCBs total 4 ways /12 Poles, with door, 1.2mm thickness surface/flush mounted, IP 43 Protection on iron/GI frame (vertical busbar type) as per specification no. SW-SWR/MCBDB | 1 | Nos.
Incoming :-
|  | Providing & erecting 3 Pole MCCB, 415V, 200A, rated short-circuit breaking capacity 25 kA (Ics=100% of Icu), adjustable thermal (overload) setting and adjustable magnetic setting with provided leads, provision for installation of shunt/UV/trip alarm contact and MCCB should have phase barriers both sides, with insulation withstand capacity 800V, no line-load bias in provided enclosure/panel as per specification no. SW-SWR/MCCB | 1 | Nos.
Outgoing :-
|  | Supplying, erecting & marking TPMCB 40A to 63A, with rated short - circuit breaking capacity (Icn) 10kA in provided distribution board as per specification no. SW-SWR/MCB | 2 | Nos.
UPS O/P DB
1.1 |  | Supplying & erecting triple pole and neutral distribution board (TPNDB), SP/TP MCBs total 4 ways /12 Poles, with door, 1.2mm thickness surface/flush mounted, IP 43 Protection on iron/GI frame (vertical busbar type) as per specification no. SW-SWR/MCBDB | 1 | Nos.
Incoming :-
|  | Supplying, erecting & marking TPMCB 40A to 63A, with rated short - circuit breaking capacity (Icn) 10kA in provided distribution board as per specification no. SW-SWR/MCB | 2 | Nos.
Outgoing :-
|  | Supplying, erecting & marking TPMCB 40A to 63A, with rated short - circuit breaking capacity (Icn) 10kA in provided distribution board as per specification no. SW-SWR/MCB | 1 | Nos.
|  | Supplying, erecting & marking TPMCB 6A to 32A, with rated short - circuit breaking capacity (Icn) 10kA in provided distribution board as per specification no. SW-SWR/MCB | 2 | Nos.
UPS DB
1.1 |  | Supplying & erecting triple pole and neutral distribution board (TPNDB), SP/TP MCBs total 4 ways /12 Poles, with door, 1.2mm thickness surface/flush mounted, IP 43 Protection on iron/GI frame (vertical busbar type) as per specification no. SW-SWR/MCBDB | 1 | Nos.
Incoming :-
|  | Supplying, erecting & marking TPMCB 40A to 63A, with rated short - circuit breaking capacity (Icn) 10kA in provided distribution board as per specification no. SW-SWR/MCB | 1 | Nos.
Outgoing :-
|  | Supplying, erecting & marking TPMCB 6A to 32A, with rated short - circuit breaking capacity (Icn) 10kA in provided distribution board as per specification no. SW-SWR/MCB | 2 | Nos.
2 |  | SITC of Electric Traction Passenger Lift with · Rated capacity :- 13 Passenger/884Kg · Floors :- G+1 floor (2 Stops/2 Landings) · Travel :- 3 to 4.2 mtrs. · Location of Lift Machine:- MR/MRL · Rated speed :- 1.0mps VS · Car/Landing door clear opening of 900/1000 mm wide x 2000 mm high · Clear Car size of ......mm wide x ......mm deep x 2250mm high · Lift shaft available having clear size of ......mm wide x mm deep, ......mm Pit depth, mm Overhead. · Doors type :- COPO/TOPO Doors with frame made from SS 304 grade solid(non-cladded) sheet of 1.5mm thick in hairline finish for car and all landing doors with SS door architraves/frames The lift doors shall have minimum 1 hour fire rating (with submission of necessary valid test certificate issued by NABL accredited or Independent test laboratory). · Lift car enclosure made from SS 304 grade solid (non-cladded) sheet of 1.5mm, thick with hairline finish with frame made from MS girders, bracing of adequate size with minimum safety factor of 5, with Toe Guard Apron, with necessary false ceiling with adequate LED lights, blower/fan for ventilation & SS chequered plate flooring, handrails, mirror, emergency light etc. The lift car interior design shall be done as per the directions of engineer in charge. · COP with SS face plate having metallic push buttons with Braille code & luminous indicator around button with FPI, scrolling UP/DN LED indicator & with / without attendant key switch, OWD with audio- visual alarm, VAS in Marathi, Hindi & English with intercom system with telephone instrument in Lift car, LMR & FCC/ground floor. · LOP with SS face plate having recess/surface push button box for all landings with scrolling UP/DN LED indicator having metallic push buttons with Braille code & luminous indicator around button with CPI, Lift car arrival & next travel direction audio-visual indication at all landings. | 4 | Nos.
|  | ADDITIONAL(9FLOOR) FOR EACH FLOOR | 9 | Nos.
A |  | Fixtures & Fans
1 |  | Supplying and erecting LED Panel Light(600mm X 600mm) Max. 35 W having CRCA powder coated housing, polystyrene diffuser having system lumens output of Min 4200 Lumens, min. efficacy of 120 lumen/W, CRI>80, CCT upto 6500K, Beam Angle of 120 deg., max. ripple of 5%, THD<10%, p.f.>0.95, operating range of 120-270V, surge protection of 2.5 kV, Life class of 50,000 Hrs. at L70B50 including driver, having mounting arrangement with board for surface type or spring loaded mounting clips complete with 3 years warranty. | 339 | Nos.
2 |  | Supplying and erecting LED square / circular Max. 14 W down lighter/Panel Light having pressure die-cast aluminium housing, polystyrene diffuser having system lumens output of Min. 1500 Lumens, min. efficacy of 110 lumen/W, CRI>80, CCT upto 6500K, Beam Angle of 120 deg., max. ripple of 5%, THD<10%, p.f. >0.95, operating range of 120-270V, surge protection of 2.5 kV, Life class of 50,000 Hrs. at L70B50, including driver, having mounting arrangement with board for surface type or spring loaded mounting clips complete with 3 years warranty | 292 | Nos.
3 |  | Supplying and erecting LED square / circular Max. 7W down lighter/ Panel Light having pressure die-cast aluminium housing, polystyrene diffuser having system lumens output of Min. 770 Lumens, min. efficacy of 110 lumen/W, CRI>80, CCT upto 6500K, Beam Angle of 120 deg., max. ripple of 5%, THD<10%, p.f. >0.95, operating range of 120-270V, surge protection of 2.5 kV, Life class of 50,000 Hrs. at L70B50, including driver, having mounting arrangement with board for surface type or spring loaded mounting clips complete with 3 years warranty. | 132 | Nos.
|  | Supplying and erecting regular/ standard model ceiling fan of 600mm. sweep complete erected in position as per specification no. FG-FN/CF | 12 | Nos.
4 |  | Supplying and erecting regular/ standard model ceiling fan of 1400mm. Sweep complete erected in position as per specification no. FG-FN/CF | 51 | Nos.
5 |  | Supplying & erecting decorative pre-wired box type fitting/batten suitable for 4 feet, T8 LED tube light (excluding tube light). | 248 | Nos.
6 |  | Supplying & erecting decorative pre-wired box type fitting/batten suitable for 4 feet, T8 LED tube light (excluding tube light). | 28 | Nos.
7 |  | Supplying & erecting 20 SWG G.I sheet metal cawl rectangular / round shaped with 25 x 25x 3 (mm) angle iron frame, metal mesh to avoid birds entry with necessary material, suitable for exhaust fan of 300 mm as per specification no FGFAS/MSC | 44 | Nos.
8 |  | Supplying and erecting integrated LED Bollard Cylindrical/Cubical shaped 800mm 8W IP65 & IK10 class having extrusion aluminium housing with polycarbonate diffuser, having system lumens output of Min. 800 Lumens, min. efficacy of 100 lumen/W, CRI>80, CCT upto 6500K, THD<10%, p.f. >0.90, operating range of 140-240V, inbuilt surge protection of 2 kV, Life class of 25,000 Hrs. at L50B50, including driver complete with 2 Year warranty as per specification No FG-ODF/FLS2. | 11 | Nos.
9 |  | Supplying and erecting integrated LED street light fitting 100-110W IP65 &IK08 class having single piece pressure die-cast aluminium housing, havingsystem lumens output of Min. 11000 Lumens, min. efficacy of 110 lumen/W, CRI>70, CCT upto 6500K, THD<10%, p.f. >0.95, operating range of 140-270V, inbuilt surge protection of 10 kV, Life class of 50,000 Hrs. at L70B50, including driver complete with 3 Years warranty as per specification No FG-ODF/FLS2. | 7 | Nos.
EXTERNAL ELECTRIFICATION
HT WORK
1 |  | Supplying, installing, testing and commissioning SF 6 Insulated 22kV, 630A, 16kA/3sec, 2 way outdoor, extensible motorised SCADA compatible RMU, internal arc tested as per electric supply company specification consisting of 1no. feeder with 1 LBS and 1 no. feeder with 1 VCB compliant to IEC 62271 - 100, 200 and 102, as per specification no. SW-HTS/RMU SCADA | 1 | 1
2 |  | Supplying, erecting, testing and commissioning 22KV HT metering cubical (compact type) approved by MSEDCL / licensee fabricated with 2 mm (14SWG) M.S. sheets with supporting angle, painted with powder coating / epoxy paint of required shade, copper bus bar size 25 x 6 mm, heavy duty mechanical lock, with counter meter for measuring no. of times the opening of meter door, top side cover (CT, PT cover) interlock with meter door, epoxy casted 3 nos. CT having required ratio between 25/5A to 200/5A, VA 10 or 15, Class 0.2S, epoxy casted 3 nos. PT having ratio 22000/V3/110/V3 VA 50, Class 0.2 suitable for provided trivector meter, and provision for incoming and outgoing cables complete duly tested by licensee with necessary test certificates and erected on provided plinth/ cc foundation | 1 | 1
3 |  | Supplying, installing, testing and commissioning SF 6 Insulated 22kV, 630A, 16kA/3sec, 1 way outdoor, extensible motorised SCADA compatible RMU, internal arc tested as per electric supply company specification consisting of 1 no. feeder with 1 VCB compliant to IEC 62271 -100, 200 and 102, as per specification no. SW-HTS/RMU SCADA
4 |  | Supplying, installation, testing and commissioning 3 phase, 22/0.433 kV, 50 Hz., 630 kVA, indoor type, vacuum cast coil (VCC) dry type cast resin Transformer, Copper wound , Dyn11 vector group, delta/star connection withadditional neutral brought out on load side, for indoor use continuous duty, average temp rise of winding (at Principal Tap) 115°C at ambient temp max 50°C & Min -5°C at full load rating, with tapping( with off circuit bolted links type tap changer) for off load +5 to - 5% @ 2.5% in +2/-2 steps, HV variation, class of insulation H/H, method of cooling AN, no load loss at rated voltage & frequency (+15% IS Tol) 2.50 kW, full load loss at rated current 5.50 kW, with 98.75 % efficiency at full load & 98.78 % at 1/2 full load, with 125 kV peak full wave lightning impulse withstand voltage with complete enclosure having IP 23 Degree of protection, cable box arrangement at HV side & bus duct at LV side,with rating & diagram plate, base channel, lifting lugs, earthing terminals & WTI scanner with 3 PT-100 sensors, etc. standard accessories complete with test certificate (as per IS:11171 & IEC 60076-11) with necessary permissions of Electrical Inspector, as per specification no. SS- TR. | 1 | 1
5 |  | Supplying , erecting & terminating XLPE insulated galvanised steel formed wire armoured (strip) cable, 22 kV(E), 3 x 120 sq. mm. aluminium conductor laid in provided trench / pipe as per specification no. CB- HT | 85 | Mtrs
End jointing of 1 KV, H.V. Cable for panels / Transformer etc. using shrinkable H.V. Joint kits, complete with all insulating material, termination, lugs etc. for following
6 |  | Providing and erecting Heat shrinkable outdoor termination kit for 11 kV (UE)/ 22 kV ( E ) XLPE HT cable 3x120 to 185 sq. mm. with necessary material as per specification no. CB-JT/HT | 2 | Nos.
7 |  | Providing and erecting Heat shrinkable indoor termination kit for 11 kV (UE)/ 22 kV ( E ) XLPE HT cable 3x120 to 185 sq. mm. with necessary material as per specification no. CB-JT/HT | 6 | Nos.
8 |  | EARTHING : Supply, installation, testing, commissioning of Electrode eathing (pipe in pipe technology.) Below ground level confirming to IS 3043 with all the required materials like chemical compound / charcoal, salt, brass nut bolts and washers, concrete chamber, heavy MS chequred cover plate and excavation in all types of soil / rock if any.
Note : 1. The chamber cover and frame shall withstand the load of fire engine and shall be got approved by consultants / Architects. 2. Measurement of resistance of each earth station and resistance of complete scheme of earthing layout must be measured, recorded and got approved by Consultants / Architects.
8.1 |  | Supplying, installation and testing of maintenance free earthing comprising of Electrode of 17.2 mm diameter Low Carbon Steel with 250 micron molecu copper bonded earthing rod of Length 3m along with 25 kg Carbon based environment friendly back fill ground enhancing compound required to fill up the excavated earth with required quantity complete, and recording the results Specification no. EA- MOBI | 25 | Nos.
8.2 |  | Supplying and erecting GI strip of high purity required size used for earthing on wall and/or any other purpose with necessary GI clamps fixed on wall painted with bituminous paint with joints required. As per specification no EA-EP. | 1200 | Kg
8.3 |  | Supplying and erecting copper strip of high purity required size used for earthing on wall and/or any other purpose with necessary copper clamps fixed on wall painted with bituminous paint with joints required. As per specification no. EA- EP. | 270 | Kg
8.4 |  | Supplying, erecting & terminating XLPE insulated unarmoured cable 1100 V. 1 core 25 sq. mm. copper conductor complete erected with provided lugs, laid in provided control panel /distribution boards / pipe as per specification no. CB- LT/CU | 200 | Mtrs
8.5 |  | Supplying & erecting conventional spike type air termination suitable to carry lightning stroke made up of heavy gauge 40 mm dia copper pipe of standard length with 5 Nos. copper spikes fixed on copper ball as air terminals duly threaded in copper pipe erected on provided foundation complete. | 4 | Nos.
8.6 |  | Supplying, erecting & terminating XLPE insulated unarmoured cable 1100 V. 1 core 25 sq. mm. copper conductor complete erected with provided lugs, laid in provided control panel /distribution boards / pipe as per specification no. CB- LT/CU | 150 | Mtrs
8.7 |  | Supplying and erecting GI strip of high purity required size used for earthing on wall and/or any other purpose with necessary GI clamps fixed on wall painted with bituminous paint with joints required. As per specification no EA-EP. | 240 | Kg
8.8 |  | Supplying, erecting & terminating XLPE insulated unarmoured cable 1100 V. 1 core 70 sq. mm. copper conductor complete erected with provided lugs, laid in provided control panel/distribution boards / pipe as per specification no. CB- LT/CU | 150 | Mtr.
8.9 |  | Supplying, erecting & terminating XLPE insulated unarmoured cable 1100 V. 1 core 50 sq. mm. copper conductor complete erected with provided lugs, laid in provided control panel /distribution boards / pipe as per specification no. CB- LT/CU | 1 | Mtr.
Substation Auxiliaries : Safety Equipment
9 |  | Providing pair of duly tested rubber hand gloves as per IS :47705 suitabl for working up to 22 kV supply complete. | 2 | Set
10 |  | Supplying standard first aid box with necessary antiseptic cream, medicine for use on wounds due burn, crepe bandage, gauge bandage, medicated ready to use bandage (Band-Aid) adhesive tape for medicinal use, scissors, anti-septic solution, etc. (All above contents shall be of standard makes) | 2 | Nos.
11 |  | Supplying and fixing PVC synthetic elastomer electrically insulating mat with class C insulation conforming to IS: 15652 – 2006 tested having 3mm thickness up to 33 kV | 5 | m2
12 |  | Providing printed instruction chart for treating persons suffering from electric shock, printed in English & Marathi and duly laminated complete. | 2 | Nos.
13 |  | Supplying & erecting Carbon Dioxide (CO2) fire extinguisher of 4.5 kg. capacity cartridge type conform to IS 2878 /15683 complete erected with necessary clamp made from 50 x 6 mm. M. S. flat with nut & bolts routed in wall complete 98.96 % efficiency at full load & 99.10 % at 1/2 full load, with 75 kV peak full | 12 | Nos
DIESEL GENERATOR SET
14 |  | Supplying, erecting, testing and commissioning of diesel generating set with alternator of 160 kVA output continuous rating, 3 Phase, 415 V, 50c/s 0.8 p. f. A.C supply, a totally enclosed air cooled / liquid cooled multi-cylinder diesel engine developing suitable BHP at 1500 rpm with 10% overload for 1 hour in 12 hours, along with standard accessories, self-excited, self-regulated, screen protected alternator with static excitation system running at 1500 RPM as per IS 4722-2001 with voltage regulation +/- 5 %, with performance class G2 and maximum fuel consumption 27.8 Ltr/hr @75% loading. Both the engine and alternator direct coupled on a common fabricated steel base frame and mounted on anti-vibrating pads with standard control panel comprising meters, switchgears, indicators connected with suitable wires/cables, the complete set enclosed in composite Acoustic enclosure as fully assembled integral unit made of 16 SWG CRCA Sheet, sound absorbing material to restrict sound level up to 75 dB at 1.0 m, provided with first filling of oil, diesel not less than 290 Ltr etc. on provided M20 Grade CC Foundation as per specification no. GEN-DG | 2 | Nos.
15 |  | Supplying, erecting, testing and commissioning of Microprocessor based Generator Control Unit (Synchronization panel) panel suitable for diesel generating set of 320 kVA capacity Three phase, 415 Volts, 50Hz A.C. with all standard features and safeties etc as per specification no. GEN-SYNC.. | 1 | Nos.
20 |  | Crane rental charges for lifting / shifting of 160 kVA Diesel generator on top of BOI Building | 2 | Job
L.T. PANEL
21 |  | Testing and Commissioning of LT Panels fabricated out of 14/16 gauge CRCA Sheet Steel in cubicle compartments, free standing floor mounted, dust and vermin proof with reinforcement of suitable size angle iron, channel `T’ section and / or flats wherever necessary, Panel to be manufactured should be as per IEC 61439 and CPRI approved 3.15 mm thick cable gland plates shall be provided on Top & Bottom of the panels for incoming & outgoing cables. Panels shall be treated with 7 tank process, all anticorrosive process before powder coating as per specification and final approved shade. 2 Nos. Earthing terminals shall be provided for all panels. Panels shall be suitable for 415 V, 3 phase, 4 wire, 50 Hz supply system with IP54 Protection. Lifting hooks shall also be provided in all panels. Approval shall be taken for each panel in the form of shop drawings before fabrication. Galvanized hardware's with zinc passivation shall be used in fabrication of panels. As Per SLD | 1 | No.
METER PANEL
22 |  | Supply & Installation of Fabricated Ready made Metering Panels & Change Over Panel supplied by Client.
|  | Readymade Metering Panels consisting of 3 Nos. 3 Phase CT METER and 3 Nos of 3phase energy meter | 1 | Nos
METER PANEL RESEDENTIAL
23 |  | Metering Panels consisting of consisting of 11 Nos of 1phase energy meter As per SLD | 1 | Nos
24 |  | Supplying and erecting 200 kVAr, 3 phase, 50 Hz., Power contactors Derated for microprocessor APFC controller with MPP / APP type capacitor with 525 V and having minimum overcurrent capacity of 1.8 In, peak inrush current capacity 300 In and minimum life 150000 hours with , consisting of suitable steps of MPP /APP type capacitor units with detuned aluminium filter 7% reactors with circuit breaker as main incomer and MCCB for each branch protection, as per specification no CP-ED/APFC | 1 | Nos
LT Cables
Supply, installation, testing, commissioning fo 1.1 KV grade XLPE insulated, inner sheath PVC tapped extruded outer sheath PVC GI wire armoured, power cable conforming to IS 1554 / Part –I with latest amendments fixed on wall / column slab / in existing hume pipes / trench / shaft / GI pipes on 5 mm. thick GI spacers / MS flat angle min. 6 mm thick with wood screws / coach screws / anchor fastners, GI saddles min. 2 mm thick all fixing accessories or in ground at a depth of 900 mm below ground in level with existing hume pipe (generally at road crossings) level including excavation, sand bedding, laying of baked bricks on side and top, temporary re-instartment, back filling, dewatering consolidation, if necessary, disposal of excess earth with in the radius of 500mm. etc. providing brass cable number tag as per drawing, specifications and as per the instructions of Consultants / Architects and of the following sizes :
25 |  | Aluminium Armoured Cables
25.1 |  | Supplying, erecting & terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 3½ core 185 sq. mm. aluminium conductor complete erected with glands & lugs, on wall/ trusses/pole or laid in provided trench/ pipe as per specification no. CB-LT/AL | 95 | Mtr.
25.2 |  | Supplying, erecting & terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 3½ core 150 sq. mm. aluminium conductor complete erected with glands & lugs, on wall/ trusses/pole or laid in provided trench/ pipe as per specification no. CB-LT/AL | 195 | Mtr.
25.3 |  | Supplying, erecting & terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 4 core 16 sq. mm. aluminium conductor complete erected with glands & lugs, on wall/ trusses/pole or laid in provided trench/ pipe as per specification no. CB-LT/AL | 126 | Mtr.
26 |  | End jointing of XLPE Armoured / Unarmoured cable by crimping with supply of all jointing material like solder less copper socket, insulator tape, flux duplicate earthing for cable gland with 12 SWG tinned copper wire & strip ( 3 mm thick minimum), etc. as per drawings, specifications and as per the instructions of the Consultants / Architects.
Aluminium Armoured Cables
26.1 |  | 3.5 C x 185 Sq.mm Al Arm. XLPE | 20 | Nos
26.2 |  | 3.5 C x 150 Sq.mm Al Arm. XLPE | 10 | Nos
26.3 |  | 3.5 C x 95 Sq.mm Al Arm. XLPE | 8 | Nos
26.4 |  | 4 C x 16 Sq.mm Al Arm. XLPE | 20 | Nos
LIFT CABLES
27 |  | Supply & Laying of Copper Ar. Cable with fire survival characteristics in Lift shaft using GI saddle pressure etc.
28 |  | Supplying, erecting & terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 4 core 10 sq. mm. copper conductor complete erected with glands & lugs, on wall/ trusses/ pole or laid in provided trench/ pipe as per specification no. CB-LT/CU | 150 | Mtr.
LIFT SHAFT LIGHTING JOB
31 |  | Shaft lighting job using existing cable 2C x 1.5 sq.mm with fire survival characteristics on each floor providing one switch Socket Point & 1 set of Bulk Head fixture which includes 40W bulb / 18W CFL with glass cover covered with wire mesh, control switch on wooden box
31.1 |  | Light point & plug point on wooden box with 10A switch (2 Nos.) + 10A socket (1 No). | 54 | Nos.
31.2 |  | Supplying and erecting bulk head LED fitting max. 10W with high transitivity diffuser with system lumens output of min. 1100 lumens, min. efficacy of 110 lumen/W, CRI>80, CCT upto 6500K, Beam Angle of 120 deg., THD<10%, p.f. >0.95, operating range of 140-260V, in built surge protection of 2.5 kV, Life class of 50,000 Hrs. at L70B50, including driver, IP66, IK09 rated on provided PVC Block / wooden board with 3 years warranty. | 54 | Nos.
OUTDOOR LIGHTING
32 |  | Supplying and erecting integrated LED street light fitting 100-110W IP65 & IK08 class having single piece pressure die-cast aluminium housing, having system lumens output of Min. 11000 Lumens, min. efficacy of 110 lumen/W, CRI>70, CCT upto 6500K, THD<10%, p.f. >0.95, operating range of 140-270V, inbuilt surge protection of 10 kV, Life class of 50,000 Hrs. at L70B50, including driver complete with 3 Years warranty as per specification No FG-ODF/FLS2. | 7 | Nos
33 |  | Hensel make IP65 Box of 96mmX96mmX110mm + 4 Way Connector + M20 Glands | 1 | Nos
|  | Supplying and erecting integrated LED Bollard Cylindrical/Cubical shaped 800mm 8W IP65 & IK10 class having extrusion aluminium housing with polycarbonate diffuser, having system lumens output of Min. 800 Lumens, min. efficacy of 100 lumen/W, CRI>80, CCT upto 6500K, THD<10%, p.f. >0.90, operating range of 140-240V, inbuilt surge protection of 2 kV, Life class of 25,000 Hrs. at L50B50, including driver complete with 2 Year warranty as per specification No FG-ODF/FLS2. | 11 | Nos
1 |  | Design, Fabrication, Supply, Erection, Testing, Commissioning along with Five Year Operation & Annual Comprehensive Maintenance Contract for Puzzle Parking etc. complete with directions and approval of the clients & Architect etc complete.
|  | Four Wheelar Car Parking | 48 | Nos.
|  | Two Wheelar Parking | 156 | Nos.
2 |  | Design, Fabrication, Supply, Erection, Testing, Commissioning along with Five Year Operation & Annual Comprehensive Maintenance Contract for 5 Levels heavy duty Hydraulic system based Car / Vehicular Lift System within the available Shaft sizeas per drawingsand Hydraulic – 3000 kg capacity Hydraulic lift for B4+B3+B2+B1+GR+UG+1 in MS cabin & MS 6 panel Centre opening auto door. however as per the discretion, directions and approval of the clients & Architect etc complete. | 2 | Nos.
A |  | HVAC SYSTEM
1 |  | 40HP Top Discharge (20HP+20HP) Supplying, erecting, testing and commissioning of 20HP+20HP, VRF/VRV air conditioning system outdoor unit (ODU) complies type-IV OEM standards working on HFC refrigerant R410A or other required/suitable green equivalent refrigerant, for minimum cooling capacity as delivering 100% capacity at 47° C, non stop cooling even at 56° C and coefficient of performance (COP) 3.00 to 4.00, modular type vertical hot air discharge suitable for longer piping range upto 1000 metre operation in cooling mode with inverter/digital VRF/VRV technology microprocessor based control compressor starter/control panel with scroll compressor, air cooled copper condenser coil of suitable shape for increasing maximum heat transfer area, rain protection cover, built in oil separator, accumulator and oil receiver, copper tube aluminium fin air cooled condenser, condenser fan with motor suitable for 415V±10%, 50 Hz, 3 phase power supply (all suitable for high ambient conditions), internal copper refrigerant piping, internal wiring and refrigerant, etc. all housed in powder coated weather proof cabinet complete. | 1 | Nos | -
2 |  | 38 HP Top Discharge (18HP+20HP) Supplying, erecting, testing and commissioning of 18HP+20HP., VRF/VRV air conditioning system outdoor unit (ODU) complies type-IV OEM standards working on HFC refrigerant R410A or other required/suitable green equivalent refrigerant, for minimum cooling capacity as delivering 100% capacity at 47° C, non stop cooling even at 56° C and coefficient of performance (COP) 3.00 to 4.00, modular type vertical hot air discharge suitable for longer piping range upto 1000 metre operation in cooling mode with inverter/ digital VRF/VRV technology microprocessor based control compressor starter/control panel with scroll compressor, air cooled copper condenser coil of suitable shape for increasing maximum heat transfer area, rain protection cover, built in oil separator, accumulator and oil receiver, copper tube aluminium fin air cooled condenser, condenser fan with motor suitable for 415V±10%, 50 Hz, 3 phase power supply (all suitable for high ambient conditions), internal copper refrigerant piping, internal wiring and refrigerant, etc. all housed in powder coated weather proof cabinet complete. | 1 | Nos | -
3 |  | 32 HP Top Discharge (12HP+20HP) -Supplying, erecting, testing and commissioning of (12HP+20HP)., VRF/VRV air conditioning system outdoor unit (ODU) complies type-IV OEM standards working on HFC refrigerant R410A or other required/suitable green equivalent refrigerant, for minimum cooling capacity as delivering 100% capacity at 47° C, non stop cooling even at 56° C and coefficient of performance (COP) 3.00 to 4.00, modular type vertical hot air discharge suitable for longer piping range upto 1000 metre operation in cooling mode with inverter/ digital VRF/VRV technology microprocessor based control compressor starter/control panel with scroll compressor, air cooled copper condenser coil of suitable shape for increasing maximum heat transfer area, rain protection cover, built in oil separator, accumulator and oil receiver, copper tube aluminium fin air cooled condenser, condenser fan with motor suitable for 415V±10%, 50 Hz, 3 phase power supply (all suitable for high ambient conditions), internal copper refrigerant piping, internal wiring and refrigerant, etc. all housed in powder coated weather proof cabinet complete. | 1 | Nos | -
4 |  | 28 HP Top Discharge (12HP+16HP) Supplying, erecting, testing and commissioning of 12HP+16 HP, VRF/VRV air conditioning system outdoor unit (ODU) complies type-IV OEM standards working on HFC refrigerant R410A or other required/suitable green equivalent refrigerant, for minimum cooling capacity as delivering 100% capacity at 47° C, non stop cooling even at 56° C and coefficient of performance (COP) 3.00 to 4.00, modular type vertical hot air discharge suitable for longer piping range upto 1000 metre operation in cooling mode with inverter/digital VRF/VRV technology microprocessor based control compressor starter/control panel with scroll compressor, air cooled copper condenser coil of suitable shape for increasing maximum heat transfer area, rain protection cover, built in oil separator, accumulator and oil receiver, copper tube aluminium fin air cooled condenser, condenser fan with motor suitable for 415V±10%, 50 Hz, 3 phase power supply (all suitable for high ambient conditions), internal copper refrigerant piping, internal wiring and refrigerant, etc. all housed in powder coated weather proof cabinet complete. | 1 | Nos | -
5 |  | 18 HP Top Discharge (18H) Supplying, erecting, testing and commissioning of 18HP, VRF/VRV air conditioning system outdoor unit (ODU) complies type-IV OEM standards working on HFC refrigerant R410A or other required/suitable green equivalent refrigerant, for minimum cooling capacity as delivering 100% capacity at 47° C, non stop cooling even at 56° C and coefficient of performance (COP) 3.00 to 4.00, modular type vertical hot air discharge suitable for longer piping range upto 1000 metre operation in cooling mode with inverter/digital VRF/VRV technology microprocessor based control compressor starter/control panel with scroll compressor, air cooled copper condenser coil of suitable shape for increasing maximum heat transfer area, rain protection cover, built in oil separator, accumulator and oil receiver, copper tube aluminium fin air cooled condenser, condenser fan with motor suitable for | 1 | Nos | -
Supply of VRF IDU : 4 WAY CASSETTE
6 |  | 2.6 TR 4 Way Cassette - Supply, installation, testing and commissioning of VRF/VRV based ceiling suspended 4 Way cassette room/indoor unit (IDU-compact / standard size) of nominal cooling capacity 2.6TR ( 918 cfm ) having EER as per BEE standards and specifications, suitable as per site requirement with swing louvers and adjustable blades from sides. IDU with drainage arrangements, fan, refrigerant liquid and refrigerant piping, cordless remote control, and fresh air port etc. IDU shall have anti corrosive coating suitable for coastal area in all respects suitable to operate on 1-phase, 230V, 50Hz, AC supply complete. The unit consisting with any additional refrigerant and oil charge as per requirement during installation. | 2 | Nos | -
7 |  | 2.3 TR 4 Way Cassette - Supply, installation, testing and commissioning of VRF/VRV based ceiling suspended 4 Way cassette room/indoor unit (IDU-compact / standard size) of nominal cooling capacity 2.3TR ( 671 cfm ) having EER as per BEE standards and specifications, suitable as per site requirement with swing louvers and adjustable blades from sides. IDU with drainage arrangements, fan, refrigerant liquid and refrigerant piping, cordless remote control, and fresh air port etc. IDU shall have anti corrosive coating suitable for coastal area in all respects suitable to operate on 1-phase, 230V, 50Hz, AC supply complete. The unit consisting with any additional refrigerant and oil charge as per requirement during installation. | 6 | Nos | -
8 |  | 2 TR 4 Way Cassette -Supply, installation, testing and commissioning of VRF/VRV based ceiling suspended 4 Way cassette room/indoor unit (IDU-compact/standard size) of nominal cooling capacity 2.0TR (618 cfm) having EER as per BEE standards and specifications, suitable as per site requirement with swing louvers and adjustable blades from sides. IDU with drainage arrangements, fan, refrigerant liquid and refrigerant piping, cordless remote control, and fresh air port etc. IDU shall have anti corrosive coating suitable for coastal area in all respects suitable to operate on 1-phase, 230V, 50Hz, AC supply complete. The unit consisting with any additional refrigerant and oil charge as per requirement during installation. | 10 | Nos | -
9 |  | 1.6 TR 4 Way Cassette - Supply, installation, testing and commissioning of VRF/VRV based ceiling suspended 4 Way cassette room/indoor unit (IDU-compact/standard size) of nominal cooling capacity 1.6 TR (618 cfm) having EER as per BEE standards and specifications, suitable as per site requirement with swing louvers and adjustable blades from sides. IDU with drainage arrangements, fan, refrigerant liquid and refrigerant piping, cordless remote control, and fresh air port etc. IDU shall have anti corrosive coating suitable for coastal area in all respects suitable to operate on 1-phase, 230V, 50Hz, AC supply complete. The unit consisting with any additional refrigerant and oil charge as per requirement during installation. | 29 | Nos | -
10 |  | 1.3 TR 4 Way Cassette - Supply, installation, testing and commissioning of VRF/VRV based ceiling suspended 4 Way cassette room/indoor unit (IDU-compact/standard size) of nominal cooling capacity 1.3TR (512 cfm ) having EER as per BEE standards and specifications, suitable as per site requirement with swing louvers and adjustable blades from sides. IDU with drainage arrangements, fan, refrigerant liquid and refrigerant piping, cordless remote control, and fresh air port etc. IDU shall have anti corrosive coating suitable for coastal area in all respects suitable to operate on 1-phase, 230V, 50Hz, AC supply complete. The unit consisting with any additional refrigerant and oil charge as per requirement during installation. | 3 | Nos | -
COMPACT CASSETTE
11 |  | 1 TR Compact Cassette- Supply, installation, testing and commissioning of VRF/VRV based ceiling suspended 4 Way cassette room/indoor unit (IDU-compact/standard size) of nominal cooling capacity 1.0TR having EER as per BEE standards and specifications, suitable as per site requirement with swing louvers and adjustable blades from sides. IDU with drainage arrangements, fan, refrigerant liquid and refrigerant piping, cordless remote control, and fresh air port etc. IDU shall have anti corrosive coating suitable for coastal area in all respects suitable to operate on 1-phase, 230V, 50Hz, AC supply complete. The unit consisting with any additional refrigerant and oil charge as per requirement during installation. | 21 | Nos | -
12 |  | 0.8 TR Compact Cassette - Supply, installation, testing and commissioning of VRF/VRV based ceiling suspended 4 Way cassette indoor unit (IDU) compact/standard size of nominal cooling capacity 0.8TR ( 441 cfm ) having EER as per BEE standards and specifications, suitable as per site requirement with swing louvers and adjustable blades from sides. IDU with drainage arrangements, fan, refrigerant liquid and refrigerant piping, cordless remote control, and fresh air port etc. IDU shall have anti corrosive coating suitable for coastal area in all respects suitable to operate on 1-phase, 230V, 50Hz, AC supply complete. The unit consisting with any additional refrigerant and oil charge as per requirement during installation. | 15 | Nos | -
HI WALL
13 |  | 1.5 TR Hi Wall - Supply, installation, testing and commissioning of VRF/VRV based Hi-wall type indoor unit (IDU) of nominal cooling capacity 1.5TR having EER as per BEE standards and specifications with multiple speed evaporator fan with motor, copper tube aluminium fin evaporator coil, washable air filter, insulated drain tray, expansion device, cordless remote control with necessary controls, with 3-core copper flexible cord of required length and electrical terminal to receive power supply, etc. IDU shall have anticorrosive coating suitable for coastal area. Unit shall be suitable for indoor wall mounting, having an electronic control console, provided with suitable mounting brackets with any additional refrigerant and oil charge as per the requirement during installation, connected to the system complete | 5 | Nos | -
14 |  | Refnet Joints - Supplying and installation of high pressure grade required size copper connection Y or T- Joints/refnet complete erected on wall/ceiling with supports/raceways, Nitrile rubber insulation, painting etc. with brazing and testing for leakages confirming the normal operation of the VRV/VRF air conditioning system. | 85 | Nos | -
15 |  | Cordless- Supply, installation, testing and commissioning wireless remote control having colour LCD panel, real time clock, temperature limitation (16 to 30° C, functions like filter clean reminder timer suitable to communicate with wired controller complete. | 86 | Nos | -
16 |  | Central Remote controler-Supplying, erecting, testing and commissioning centralised programmable remote control panel (HMI) touch manager controls minimum 16 system of 64 ODU's can be controlled and up to 992 IDU's can be individually mounted and controlled indoor units having colour min 200mm size LCD touch panel, yearly schedule, power proportional distribution function, temperature limitation, history function complete erected on wall integrated with provided fire alarm system. | 2 | Nos | -
HI WALL - 3 star inverter
17 |  | 2 TR Hi Wall- Supplying, installing, testing & commissioning split type variable speed inverter technology with minimum 3 to 1 convertible mode for compressor, room air conditioning unit 1.7TR to 2.0TR capacity having ISEER minimum 3.8 to maximum 4.39 suitable to operate on 250V, 50 Hz, A.C. supply having 1 no of air handling unit hi-wall/floor mounting type complete with refrigerant R32 having copper condenser, minimum 2.5PM filter, self diagnosis feature, stabilizer free operation & temperature display on indoor unit, noise level maximum 50dBA at position as per specification no. APAC/ WAC | 5 | Nos | -
18 |  | 1.5 TR Hi Wall - Supplying, installing, testing & commissioning split type variable speed inverter technology with minimum 3 to 1 convertible mode for compressor, room air conditioning unit 1.5TR capacity having ISEER minimum 3.8 to maximum 4.39 suitable to operate on 250V, 50 Hz, A.C. supply having 1 no of air handling unit hi-wall/floor mounting type complete with refrigerant R32 having copper condenser, minimum 2.5PM filter, self diagnosis feature, stabilizer free operation & temperature display on indoor unit, noise level maximum 50dBA at position as per specification no. APAC/ WAC | 1 | Nos | -
REFRIGERANT COPPER PIPING
19 |  | Supplying, laying/fixing, testing and commissioning of appropriate nominal refrigerant copper pipe of 41.3mm dia (OD) for return piping of suitable gauge (hard copper pipe for liquid main line and soft copper pipe for refrigerant) along with necessary supports, hangers, clamps, vibration isolators and fittings such as bends, tees, valves, gauges, strainers with insulation of 19mm thick elastomeric nitrile rubber along with application of multicoating of VRV/VRF piping for protection against mechanical damages, fungal growth, flame spread, water permeance and ultra violet radiations with OEM standards of VRV/VRF air conditioning system complete. | 50 | Rmt.
20 |  | Supplying, laying/fixing, testing and commissioning of appropriate nominal refrigerant copper pipe of 34.9mm dia (OD) for return piping of suitable gauge (hard copper pipe for liquid main line and soft copper pipe for refrigerant) along with necessary supports, hangers, clamps, vibration isolators and fittings such as bends, tees, valves, gauges, strainers with insulation of 19mm thick elastomeric nitrile rubber along with application of multicoating of VRV/VRF piping for protection against mechanical damages, fungal | 50 | Rmt.
16 |  | Supplying, laying/fixing, testing and commissioning of appropriate nominal refrigerant copper pipe of 28.6mm dia (OD) for return piping of suitable gauge (hard copper pipe for liquid main line and soft copper pipe for refrigerant) along with necessary supports, hangers, clamps, vibration isolators and fittings such as bends, tees, valves, gauges, strainers with insulation of 19mm thick elastomeric nitrile rubber along with application of multicoating of VRV/VRF piping for protection against mechanical damages, fungal growth, flame spread, water permeance and ultra violet radiations with OEM standards of VRV/VRF air conditioning system complete. | 50 | Rmt.
17 |  | Supplying, laying/fixing, testing and commissioning of appropriate nominal refrigerant copper pipe of 22.2mm dia (OD) for return piping of suitable gauge (hard copper pipe for liquid main line and soft copper pipe for refrigerant) along with necessary supports, hangers, clamps, vibration isolators and fittings such as bends, tees, valves, gauges, strainers with insulation of 19mm thick elastomeric nitrile rubber along with application of multicoating of VRV/VRF piping for protection against mechanical damages, fungal growth, flame spread, water permeance and ultra violet radiations with OEM standards of VRV/VRF air conditioning system complete. | 150 | Rmt.
18 |  | Supplying, laying/fixing, testing and commissioning of appropriate nominal refrigerant copper pipe of 19.1mm dia (OD) for return piping of suitable gauge (hard copper pipe for liquid main line and soft copper pipe for refrigerant) along with necessary supports, hangers, clamps, vibration isolators and fittings such as bends, tees, valves, gauges, strainers with insulation of 19mm thick elastomeric nitrile rubber along with application of multicoating of VRV/VRF piping for protection against mechanical damages, fungal growth, flame spread, water permeance and ultra violet radiations with OEM standards of VRV/VRF air conditioning system complete. | 90 | Rmt.
19 |  | Supplying, laying/fixing, testing and commissioning of appropriate nominal refrigerant copper pipe of 15.88mm dia (OD) for return piping of suitable gauge (hard copper pipe for liquid main line and soft copper pipe for refrigerant) along with necessary supports, hangers, clamps, vibration isolators and fittings such as bends, tees, valves, gauges, strainers with insulation of 19mm thick elastomeric nitrile rubber along with application of multicoating of VRV/VRF piping for protection against mechanical damages, fungal growth, flame spread, water permeance and ultra violet radiations with OEM standards of VRV/VRF air conditioning system complete. | 250 | Rmt.
20 |  | Supplying, laying/fixing, testing and commissioning of appropriate nominal refrigerant copper pipe of 12.7mm dia (OD) for return piping of suitable gauge (hard copper pipe for liquid main line and soft copper pipe for refrigerant) along with necessary supports, hangers, clamps, vibration isolators and fittings such as bends, tees, valves, gauges, strainers with insulation of 19mm thick elastomeric nitrile rubber along with application of multicoating of VRV/VRF piping for protection against mechanical damages, fungal growth, flame spread, water permeance and ultra violet radiations with OEM standards of VRV/VRF air conditioning system complete. | 250 | Rmt.
21 |  | Supplying, laying/fixing, testing and commissioning of appropriate nominal refrigerant copper pipe of 9.5mm dia (OD) for return piping of suitable gauge (hard copper pipe for liquid main line and soft copper pipe for refrigerant) along with necessary supports, hangers, clamps, vibration isolators and fittings such as bends, tees, valves, gauges, strainers with insulation of 19mm thick elastomeric nitrile rubber along with application of multicoating of VRV/VRF piping for protection against mechanical damages, fungal growth, flame spread, water permeance and ultra violet radiations with OEM standards of VRV/VRF air conditioning system complete. | 300 | Rmt.
22 |  | Supplying, laying/fixing, testing and commissioning of appropriate nominal refrigerant copper pipe of 6.35mm dia (OD) for return piping of suitable gauge (hard copper pipe for liquid main line and soft copper pipe for refrigerant) along with necessary supports, hangers, clamps, vibration isolators and fittings such as bends, tees, valves, gauges, strainers with insulation of 19mm thick elastomeric nitrile rubber along with application of multicoating of VRV/VRF piping for protection against mechanical damages, fungal growth, flame spread, water permeance and ultra violet radiations with OEM standards of VRV/VRF air conditioning system complete. | 300 | Rmt.
ELECTRICAL CABLING FOR CONNECTING IDU TO ODU
23 |  | SITC of 3 core 1.5sqmm cable for VRF System - Supplying and erecting PVC insulated PVC round sheathed 1.5 sq.mm (30 no. x0.25 mm dia.) 3 core flexible multi stranded copper Industrial cable for voltage grade up to 1.1 kV | 150 | Rmt.
24 |  | PVC Conduit for Communication cable-Supplying and erecting HMS PVC conduit FRLS grade 25 mm dia. with necessary accessories in wall/floor with chiselling appropriately as per specification No: WG- MA/CC. | 150 | Rmt.
25 |  | SITC of 2 core 1.5sqmm cable for DX System- Supplying, erecting & terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 2 core 2.5 sq. mm. copper conductor complete erected with glands & lugs, on wall/ trusses/ pole or laid in provided trench/ pipe as per specification no. CB-LT/CU | 1500 | Rmt.
DRAIN PIPING & TOILET EXHAUST
26 |  | Supply and installation of 32 mm dia Drain piping in hard PVC with 9mm insulation sleave and all fittings, supports and clamps | 200 | Rmt.
27 |  | Supply and installation of 25 mm dia Drain piping in hard PVC with 9mm insulation sleave and all fittings, supports and clamps | 200 | Rmt.
28 |  | Supply and installation of 40 mm dia Drain piping in hard PVC with 9mm insulation sleave and all fittings, supports and clamps | 150 | Rmt.
29 |  | Supplying and erecting circular flexible/rigid PVC pipe duct of size 150mm dia, 4mm thickness with required couplers, reducers, T-joints, Y-joints elbows and necessary supports etc. with sealing with provided control/air flow regulating valves/dampers, filters at position complete. | 100 | Rmt.
30 |  | Supplying and erecting circular flexible/rigid PVC pipe duct of size 100mm dia, 4mm thickness with required couplers, reducers, T-joints, Y-joints elbows and necessary supports etc. with sealing with provided control/air flow regulating valves/dampers, filters at position complete. | 240 | Rmt.
Ventilation Fans
31 |  | Supplying, erecting, testing & commissioning fresh air intake system, ductable circular inline fresh air fan inlet unit having 1000 cfm capacity with maintaining the static pressure minimum 20mm suitable to operate on 1 phase, 230 v 50 hz AC supply | 5 | Nos
32 |  | Supplying, erecting, testing & commissioning fresh air intake system, ductable circular inline exhaust fan inlet unit having 300 cfm capacity with maintaining the static pressure minimum 20mm suitable to operate on 1 phase, 230 v 50 hz AC supply | 11 | Nos
Ducting Rectangular ducting
33 |  | Ducting 0.60 mm ( 24 SWG ) Rectangular ducting - Supplying and erecting GI sheet 0.6 mm (24 SWG) having zinc coating of 275 microns with galvanization process compliance to IS 2629:1985 to be used for fabrication of boxes panel boards etc. including cutting, bending, drilling, welding, riveting etc. and painting with one coat of red lead paint and 2 coats of enamel paint. | 300 | sqm
34 |  | Canvass- Supply, fabrication, installation and testing of flexible canvas connections constructed between ductable unit/dampers/ducting of suitable size with fire resist flexible double canvas sleeve complete. | 5 | Nos | -
35 |  | Birdmesh- Supplying and fixing wire mesh (Jali) cover suitable for fitting / fan or for any purpose, complete with necessary materials. The jali cover shall be made from good quality G.I. wire mesh size 25 x 25 (mm) and made up of 14 SWG G.I. wire with side / supporting MS strips of suitable size. | 5 | Nos | -
36 |  | Supply and installation of PVC disc valve for toilet exhaust | 60 | Nos | -
37 |  | Supplying and erecting circular flexible/rigid PVC pipe duct of size 100mm dia, 4mm thickness with required couplers, reducers, T-joints, Y-joints elbows and necessary supports etc. with sealing with provided control/air flow regulating valves / dampers, filters at position complete. | 100 | Rmt | -
Basement Ventilation
Fans
38 |  | Tube Axal Fan - 8500 CFM , 30mm ESP VFD Compatible- For Fresh Air - Supply, installation, testing & commissioning of Tube Axial Flow Fan of adjustable pitch , the blade of the fan shall be made out of Die cast alluminium alloy duly dynamically and statically balanced mounted directly on TEFC Sq. Cage Induction Motor suitable for 3 phase 415 V ±10% 50 C/S AC supply with cylindrical casing & motor support. All Exhaust Fans Motor and Cabinet shall be suitable For smoke exhaust application & thermally rated For 250 Deg.C For 2 hours as per EN-12101-3 2002. Fresh Air Fans are with Class F motor. Fan casing HOT DIPPED GALVANISED.Fan capacities based on following details complete as per specification.Fans to be mounted on vibration isolators. Make: Kruger/Systemair/ Greenheck/Nikotra/LTI | 2 | Nos | -
39 |  | Tube Axal Fan - 20000 CFM , 30mm ESP VFD Compatible- For Fresh Air ( Staircase and lift lobby )- Supply, installation, testing & commissioning of Tube Axial Flow Fan of adjustable pitch , the blade of the fan shall be made out of Die cast alluminium alloy duly dynamically and statically balanced mounted directly on TEFC Sq. Cage Induction Motor suitable for 3 phase 415 V ±10% 50 C/S AC supply with cylindrical casing & motor support. All Exhaust Fans Motor and Cabinet shall be suitable For smoke exhaust application & thermally rated For 250 Deg.C For 2 hours as per EN-12101-3 2002. Fresh Air Fans are with Class F motor. Fan casing HOT DIPPED GALVANISED.Fan capacities based on following details complete as per specification.Fans to be mounted on vibration isolators. Make: Kruger/Systemair/ Greenheck/Nikotra/LTI | 4 | Nos | -
40 |  | Tube Axial Fan - 8500 CFM 30mm ESP VFD Compatible-Normal Exhaust and smoke exhaust - Supply, installation, testing & commissioning of Tube Axial Flow Fan of adjustable pitch , the blade of the fan shall be made out of Die cast alluminium alloy duly dynamically and statically balanced mounted directly on TEFC Sq. Cage Induction Motor suitable for 3 phase 415 V ±10% 50 C/S AC supply with cylindrical casing & motor support. All Exhaust Fans Motor and Cabinet shall be suitable For smoke exhaust application & thermally rated For 250 Deg.C For 2 hours as per EN-12101-3 2002. Fresh Air Fans are with Class F motor. Fan casing HOT DIPPED GALVANISED.Fan capacities based on following details complete as per specification.Fans to be mounted on vibration isolators. Make: Kruger/Systemair/ Greenheck/Nikotra/LTI | 2 | Nos | -
41 |  | Jet Fan -Supply, installing, testing and commissioning of Ductless Ventilation / Jet fans, 450 mm dia,as per specifications for Normal ventilation and Smoke Extraction application Fan Shall be suitable for 300° C for 2hrs operation.Dual Speed Motor-TECHO MakeFan speed shall not exceed 1450 RPM & outlet velocity shall be less than 10 m/s (for NORMAL Mode as well asFIRE Mode application). Motor with class H isulation. Fan shall be fire rated at 250°C for 120 minutes. The minimum external fan static shall be as explained in the technical specifications. All unit shall be suitable for outdoor installation, Mounting feet, Spring type vibration isolator, aluminum wire mesh bird screen at discharge of fan and MS Powder coated Protection net on free suction, Heavy duty flexible double layer canvas connection. Fan GAD to be submited for confirmation on fan mounting (Ceiling suspended, Floor mounted or vertical installation). SITC of Jetfans for Basements LEVEL with Isolator Spring Note : (ID- 400 mm, OD- 500 mm Dia) Jetfans are designed to run at 300 Deg. C for 2 Hours incase of emergency Motor : Capacity to be confirmed by vendor Scope of Supply : Jetfan with dual speed motor suitable for 300 Deg C for 2 Hours, 2 silencers, 2 bird screen and 2 nos. mounting legs & Inlet Bellmouth only. | 4 | Nos | -
42 |  | Canvass- Supply, fabrication, installation and testing of flexible canvas connections constructed between ductable unit/dampers/ducting of suitable size with fire resist flexible double canvas sleeve complete. | 8 | Nos | -
43 |  | Birdmesh-Supplying and fixing wire mesh (Jali) cover suitable for fitting / fan or for any purpose, complete with necessary materials. The jali cover shall be made from good quality G.I. wire mesh size 25 x 25 (mm) and made up of 14 SWG G.I. wire with side / supporting MS strips of suitable size | 4 | Each | -
PLC Panel
44 |  | LOGIC CONTROL PLC PANEL to Control Start/Stop & speed change in all fans in basement including Jet Fans, fans from Low to high speed based on the CO Level in the Basement. All these fans should also be SWITCHED on in full speed incase of receipt of FIRE Signal. The Logical Operation of NORMAL mode and FIRE mode is desired from PLC. Vendor Should submit SLD and GA drawings for Consultants approval. Compartmentalized Electrical MCC Panel as per IS standard 8623 with Protection Class of IP 56 and Fault level of 25kA. The panel made out of 14 SWG CRCA sheet finished with Siemens Grey Painting. The Panel consists suitable Incomer from Fire Emergency panel. Outgoing Feeders along with Starters for 2B Basement exhaust ,fresh and jet fans and Basement1 exhaust,fresh and jet fans and also to fire mode exhaust fans at lower ground floor with 2 nos. spare feeders, MCCB, metering Panel, top cable entry, aluminium bus bar and custom built PLC logic controller with necessary control wiring etc. Each Feeder shall have TPN MCB, two Starters and indication lamps, toggle switch for two speed operations and Electrical interlock for two speed functions. It Should control the JET Fans for demand ventilation with a Logic. 25 % Consider on Higher Side for All Switch Gear ,All Cable should have Copper Polycab only , Each level panel on / off / Trip have Dual Realy for BMS Provision . Entire Panel should be TYPE 2 Co-ordination only Acceptd . Material is to use as Per Make List only .. All System is to operated on Touch Panel HMI only . | 1 | Nos | -
45 |  | CFD Analysis | 1 | Lot | -
CO Sensors
46 |  | Supply, Installation, Testing & Commissioning of CO Sensors | 3 | Nos | -
Supply, Installation, Testing & Commissionin of Cables
47 |  | 6 C× 1.5 SQMM Cu . armoured cables for Jet fan -Supplying, installing, testing and commissioning FR, XLPE armoured cable 8 core 1.5 sq.mm. copper conductor complete erected on wall/ ceiling complete as per specification no. CB-LT/CU | 240 | Rmt | -
48 |  | 3 C× 8 SQMM Cu . armoured cables for Axial fan ( Vendor to confirm Cable Size as per fan selection)- Supplying, erecting & terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 3 core 10 sq. mm. copper conductor complete erected with glands & lugs, on wall/ trusses/ pole or laid in provided trench/ pipe as per specification no. CB-LT/CU | 285 | Rmt | -
49 |  | 4 C× 0.75 SQMM Cu . armoured cables for Co-sensors - Sheilded - Supplying, erecting & terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 4 core 4 sq. mm. copper conductor complete erected with glands & lugs, on wall/ trusses/ pole or laid in provided trench/ pipe as per specification no. CB-LT/CU | 200 | Rmt | -
Ducting
50 |  | Supply, Installation, Testing & Commissioning of Ducting for Tube Axial Fans - Ducting 0.70 mm ( 22 SWG ) Rectangular ducting- Supplying and erecting GI sheet 0.8 mm (22 SWG) having zinc coating of 275 microns with galvanization process compliance to IS 2629:1985 to be used for fabrication of boxes panel boards etc. including cutting, bending, drilling, welding, riveting etc. and painting with one coat of red lead paint and 2 coats of enamel paint. | 200 | Sqmt | -
|  | ELECTRICAL TOTAL AMOUNT |  |  |  | 0

## conference room
Conference Room
S.no. | DSR-2022 | Description | Qty | Unit | Rate | Amount
1 |  | Control unit shall controls up to 100 discussion units with Cascade capability to handle upto 300 discussion units and a max of six interpretation units for upto 3 spoken languages in the meeting. Unit cunit shall come with inbuilt Voting function. Controller shall have Built-in feedback suppressor. Controller shall comes with Built-in recording for up to 65,000 hrs on USB. The control unit can also be programmed to work via Web Remote Control, which enables the user to configure and operate the system from a computer or mobile device. IP Control allows full parameter access from most third-party control systems. Frequency response - + 1.0, – 2.0dB, 20Hz~20kHZ or better, Dynamic range 110dB, Signal to noise 90dB, THD Less than 0.03% @1kHz unity. | 1 | Nos. |  | 0
2 |  | Under the table discussion unit placed anywhere in same chain/loop with other ATUC-50 units, seven Euroblock connectors for audio and control options, and six Euroblock connectors for LED power and general-purpose input/output (GPIO). Under Table Unit shall include Includes mic input, speaker output, headphone output, control input (Talk On, Vol. Up, Vol. Down, Channel Select – Open/Closed contact), LED status output, GPIO. Frequency response 20Hz – 20kHz, Sampling Frequency 24bit / 48kHz, Phantom Power DC + 48V, Signal-to-Noise Ratio 86dB, Connections 2x RJ45, 39 pin on EuroBlock. Unit shall be available in single version and programmable per user type as delegate, chairman or VIP. | 17 | Nos. |  | 0
3 |  | Surface-mount boundary Microphone with permanently polarized condenser element, Cardioid/Omnidirectional Polar pattern, 70 to 15,000 Hz frequancy response, 110 dB dynamic range, 70 dB SNR, 5-pin XLR-M type output connector. Microphone shall come with Logic I/O capability to control of remote devices. Microphone switch shall be touch-sensitive capacitive-type with two-state RGB LED ring and shall have option for seven or more selectable colors + OFF to indicates mic status. Microphone shall have RFI-shielding technology and shall be RoHS compliant. | 17 | Nos. |  | 0
4 |  | Supply of Vocal set with Carrier frequency: Digital 2.4 GHz. Encryption: 256-bit AES Simultaneous operation: Yes, up to 4 coexisting systems Working range: 100 ft. (30 m) Latency: <=2.9 ms Frequency/channel selection: Adaptive channel selection Diversity wireless: Antenna, time, frequency Frequency response: 70 Hz–20 KHz +1/-3 dB Dynamic range: 116 dB @ 1 KHz Signal-to-noise: >90 dBA Transmitter battery: 2x AA alkaline Battery life: 9 hours Approx. | 2 | Nos. |  | 0
5 |  | Supply of Fixed I/O DSP with 12 analog inputs, 8 analog outputs, 8 channels configurable USB audio, AEC technology (all 12 inputs), 2 channel VoIP, and standard FXO telephone interface | 1 | Nos. |  | 0
6 |  | Supply of wall mount speaker with Rated input: 100V/ 15W, Sensitivity: 92dB Frequency response: 60~20KHZ, Speaker unit: Two-way (6.5” Woofer/ Tweeter), Box material: ABS cabinet. | 6 | Nos. |  | 0
7 |  | Supply of Two channels model: 120W@8Ω<1% THD+N 120W@4Ω<1% THD+N 240W Bridged 70V/100V <1% THD+N. Adaptable with 4-8 Ohm loads. Bridged mode 240W output for 70V or 100V loudspeakers (direct drive). Power down after 15 minutes of no signal and comply with Energy Star Power consumption limits of < 0.5W in standby. LED at the front panel to indicate the current operation status. Frequency Response : 20Hz-20kHz, +/- 2dB@4Ω Load. Signal to Noise: >90dB@1W (20Hz-20kHz). Input Sensitivity: 1V (+2.2dBu)@Max Output 4Ω. Gain Value: 25db @ 4 Ohm. | 1 | Nos. |  | 0
8 |  | Supply of table top cable manager with 2 x universal Power socket, with Net Line, HDMI line, VGA line, 3.5mm Line. | 4 | Nos. |  | 0
9 |  | Supply of UHD+ 2x1 HDMI/VGA to HDMI Scaler,Switchable HDMI input and VGA input with a 3.5mm analog stereo audio input . Supports up to 4K UHD (18Gbps, 4K@50/60Hz 4:4:4, 8-bit) video input and output over HDMI . Supports up to 1080p or WUXGA (1920x120060Hz RB) video input over VGA. Auto input switching by detecting HDMI/VGA signal. | 4 | Nos. |  | 0
10 |  | Supply, installation, testing & commissioning of Four Input SuperSpeed USB Switcher, RS232 for control. | 1 | Nos. |  | 0
11 |  | Supply of HDMI TX/RX extender with 3D, 4K×2K support, HDCP and DVI compliant Complies with the HDBaseT technology. Supports HDMI (including HDCP) over a single CAT5e/6 up to 70m. Full HD resolution support (1080p@60Hz/36-bit), 3D and 4Kx2K over 40m and PC resolution support (VGA to WUXGA) over CAT5e/6 cable. HDMI input up to 15m with 8-bit resolution or 10 m with 12-bit resolution. HDMI output up to 15 m with 8/12-bit resolution . Multiple control interfaces such as RS-232 with baud rate up to 115200/sec and IR. Supports HDCP repeater and CEC bypass. Supports High Definition LPCM 7.1CH, Dolby TrueHD, Dolby Digital Plus and DTS-HD Master Audio transmission. | 4 | Nos. |  | 0
12 |  | Supply of Four HDMI inputs matrixed to four HDMI outputs with HDMI 2.0a specification and 18Gbps (600MHz) 4K UHD support, HD resolutions up to 3840×2160@60Hz (4:4:4, 8-bit) & 4096×2160@60Hz (4:4:4, 8-bit), 16-bit Deep Color up to 1080p@60Hz. Four Audio output ports can pair with Four HDMI outputs individually. Audio support Digital and analog Formats. Device should be provides an intuitive set of front panel controls with an LCD as well as RS-232, Telnet, WebGUI, and IR remote control options. | 1 | Nos. |  | 0
13 |  | •12x Optical zoom •73° wide-angle view with auto-focus •USB 3.0, HDMI, & IP output •Full HD 1080p60 •Control: Remote control, USB (UVC), RS-232 •Pan/Tilt Angles: ±170°, Tilt: -30° to +90° VIDEO CHARACTERISTICS •Resolution up to 1080p @ 60 fps •H.261, H.263, H.263+/++ •H.264/AVC High Profile – up to 6Mbps •H.264/SVC (Skype for Business) DATA CHARACTERISTICS •H.239 support for data sharing •Resolution up to 1080p •Data inputs via HDMI, Wireless, USB. Video inputs: 2x HDMI (SIP/H.323, Skype for Business), 2x USB •Video outputs: 1x HDMI, 1x Display port •Audio inputs: Balanced audio, USB, Line in •Audio outputs: Balanced audio, Line out, RECORDING •Formats: MP4, WMV •Storage options: Local, external, network (NAS) | 1 | Nos. |  | 0
14 |  | VideoWall Screen Size of LED Screen 24 Ft x 8 Ft (±2 Inch) Pixel Pitch ( mm) 1.5 LED Type ( black or white SMD/TH ) black SMD LED package Nichia/Cree/Osram/Nationstar Pixel Configuration 1R1G1B Pixel Density ( pixel/m2) 640000 or better Brightness 600 nits or better ColorTemperature 3200-9300K Adjustable Gamma Default 2.8 Dimming Capability 0%-100% Contrast Ratio 7000:1 Refresh rate 3840hz Colors 4.39 trillion Viewing Angle Horizontal 160 Viewing Angle Vertical 160 Lifetime 100000 Power Input 220VAC±15% Power Max. ( W/Cabinet) 125 Power Avg. (W/Cabinet) 65 Cabinet mm WxHXD 600x337.5x40.5 Cabinet Resolution 480x270 Module mm WxHxD 150x337.5x2.5 Module Resolution 120x270 Temperature Operation 0℃~35℃ , Temperature Storage -20℃~60℃ , Relative Humidity Storage 10%-90% RH , Service Access Front IP Grade Front IP30/Rear IP50 Frame Rate 30-120hz Redundancy -Power Dual Power supply Inbuilt | 1 | Nos. |  | 0
15 |  | Supply of 43" display with Brightness (cd/m2)Typical: 440, Contrast Ratio1200:1, Dynamic Contrast Ratio400,000:1, Panel Type (IPS/VA)IPS, Panel Surface Anti glare, operation Time24/7 with low profile floor mount stand. | 1 | Nos. |  | 0
16 |  | Wireless Presenter module Allows simultaneous present upto 4. Video • H.264 compression Audio • LCPM 2.0 Resolution1 • Up to 4K@30Hz Ethernet • 10/100/1000-BASE-T RJ-45 LAN Wireless • Miracast and Local Wi-Fi Mode: 802.11ac dual-band 3×3 MIMO • Network Bridge: 802.11ac dual-band 2×2 MIMO Authentication • WPA-PSK (TKIP).Interface • 1 x HDMI Input • 1 x HDMI Output • 2 x USB 2.0 Host Type-A • 1 x USB 3.0 Host Type-A • 1 x Analog 3.5mm audio output • 1 x DC Power Jack | 1 | Nos. |  | 0
17 |  | Space Controller - Controls any AV device/display with its corresponding logic. High Performance Architecture - Enables a scalable and flexible programming platform. 4 RS–232 Bidirectional Control Ports - For controlling devices via bi–directional serial control protocols. 4 IR Emitter & 1 IR Receiver Control Ports - Control devices via IR control protocols and learn commands from IR remotes. 4 GPI/O Control Ports - Control devices via general purpose I/O ports, program configured as digital input, digital output or analog input interface for controlling sensors, door locks, audio volume and lighting control devices. 4 Relay Control Ports - Control devices via relay contact closure, such as opening and closing drapes, shades, blinds, and projection screen scrolling. Resilient powering with PoE and optional PSU (not included). Network Support - 10/100/1000Mbps Ethernet. LED Indicators - I/O port state and system status. Software Management Support - Kramer Control, API. Approved Makes - Kramer / Crestron / Extron | 1 | Nos. |  | 0
18 |  | IR High accuracy High sensitivity (110 V/W) Low resistance (50 KΩ) and therefore Very good signal-to-noise-ratio Good response time (40 ms) Low cost thin film technology Connectivity sensor | 2 | Nos. |  | 0
19 |  | 6 white–color, touch–sensitive buttons Custom labeled, removable button caps 1 Ethernet port 1 KNET™ port 2 Bidirectional RS–232 ports 2 IR emitter ports 3 Relay ports 1 IR sensor for learning Site–CTRL software compatible Mounts in standard 1 gang US wall junction boxes | 2 | Nos. |  | 0
20 |  | Liquid Retina display 21.08 cm / 8.3-inch (diagonal) LED-backlit Multi-Touch display with IPS technology 2266x1488 resolution at 326 pixels per inch (ppi) Wide colour display (P3) True Tone display Fingerprint-resistant oleophobic coating Fully laminated display Anti-reflective coating 1.8% reflectivity 500 nits brightness | 1 | Nos. |  | 0
21 |  | 8 Channel - High Power (230v) relay. • Controlling Motors for up/down screen •Projector Mounting Kit up/down •Curtains open/close •Power ON the projector / switcher in sequence •Power ON/OFF the lightse | 1 | Nos. |  | 0
22 |  | DIN Rail 0-10V Dimmer Module, 4 feeds, 4 channels. Input Power •230 V~ (CE) 50 Hz •Lightning Strike Protection: Can withstand voltage surges of up to 6000 V~ and current surges up to 3000 A. 4 preset lighting scenes and off are accessible from the Control Unit front panel. •12 additional scenes are stored in the Control Unit. These scenes are accessible via Wallstations and/or Control Interfaces. •Light levels fade smoothly between scenes. Fade time can be set differently for each scene, between 0-59 sec. or 1-60 min. Fade time from Off is capped at 5 sec | 1 | Nos. |  | 0
|  | Video Conference Room |  |  |  | 0
1 |  | VideoWall Screen Size of LED Screen 135'' Diagnol Pixel Pitch ( mm) 1.5 LED Type ( black or white SMD/TH ) black SMD LED package Nichia/Cree/Osram/Nationstar Pixel Configuration 1R1G1B Pixel Density ( pixel/m2) 640000 or better Brightness 600 nits or better ColorTemperature 3200-9300K Adjustable Gamma Default 2.8 Dimming Capability 0%-100% Contrast Ratio 7000:1 Refresh rate 3840hz Colors 4.39 trillion Viewing Angle Horizontal 160 Viewing Angle Vertical 160 Lifetime 100000 Power Input 220VAC±15% Power Max. ( W/Cabinet) 125 Power Avg. (W/Cabinet) 65 Cabinet mm WxHXD 600x337.5x40.5 ,Cabinet Resolution 480x270 Module mm WxHxD 150x337.5x2.5 ,Module Resolution 120x270 Temperature Operation 0℃~35℃ ,Temperature Storage -20℃~60℃ Relative Humidity Storage 10%-90% RH ,Service Access Front IP Grade Front IP30/Rear IP50 ,Frame Rate 30-120hz Redundancy -Power Dual Power supply Inbuilt | 1 | Nos |  | 0
2 |  | •12x Optical zoom •73° wide-angle view with auto-focus •USB 3.0, HDMI, & IP output •Full HD 1080p60 •Control: Remote control, USB (UVC), RS-232 •Pan/Tilt Angles: ±170°, Tilt: -30° to +90° VIDEO CHARACTERISTICS •Resolution up to 1080p @ 60 fps •H.261, H.263, H.263+/++ •H.264/AVC High Profile – up to 6Mbps •H.264/SVC (Skype for Business) DATA CHARACTERISTICS •H.239 support for data sharing •Resolution up to 1080p •Data inputs via HDMI, Wireless, USB. Video inputs: 2x HDMI (SIP/H.323, Skype for Business), 2x USB •Video outputs: 1x HDMI, 1x Display port •Audio inputs: Balanced audio, USB, Line in •Audio outputs: Balanced audio, Line out, RECORDING •Formats: MP4, WMV •Storage options: Local, external, network (NAS) | 1 | Nos. |  | 0
3 |  | Supply of Four HDMI inputs matrixed to four HDMI outputs with HDMI 2.0a specification and 18Gbps (600MHz) 4K UHD support, HD resolutions up to 3840×2160@60Hz (4:4:4, 8-bit) & 4096×2160@60Hz (4:4:4, 8-bit), 16-bit Deep Color up to 1080p@60Hz. Four Audio output ports can pair with Four HDMI outputs individually. Audio support Digital and analog Formats. Device should be provides an intuitive set of front panel controls with an LCD as well as RS-232, Telnet, WebGUI, and IR remote control options. | 1 | Nos. |  | 0
4 |  | HDMI, VGA, Audio with 2 power sockets RJ45 . | 2 | Nos. |  | 0
5 |  | Wireless Presenter module Allows simultaneous present upto 4. Video • H.264 compression Audio • LCPM 2.0 Resolution1 • Up to 4K@30Hz Ethernet • 10/100/1000-BASE-T RJ-45 LAN Wireless • Miracast and Local Wi-Fi Mode: 802.11ac dual-band 3×3 MIMO • Network Bridge: 802.11ac dual-band 2×2 MIMO Authentication • WPA-PSK (TKIP).Interface • 1 x HDMI Input • 1 x HDMI Output • 2 x USB 2.0 Host Type-A • 1 x USB 3.0 Host Type-A • 1 x Analog 3.5mm audio output • 1 x DC Power Jack | 1 | Nos. |  | 0
6 |  | Space Controller - Controls any AV device/display with its corresponding logic. High Performance Architecture - Enables a scalable and flexible programming platform. 4 RS–232 Bidirectional Control Ports - For controlling devices via bi–directional serial control protocols. 4 IR Emitter & 1 IR Receiver Control Ports - Control devices via IR control protocols and learn commands from IR remotes. 4 GPI/O Control Ports - Control devices via general purpose I/O ports, program configured as digital input, digital output or analog input interface for controlling sensors, door locks, audio volume and lighting control devices. 4 Relay Control Ports - Control devices via relay contact closure, such as opening and closing drapes, shades, blinds, and projection screen scrolling. Resilient powering with PoE and optional PSU (not included). Network Support - 10/100/1000Mbps Ethernet. LED Indicators - I/O port state and system status. Software Management Support - Kramer Control, API. | 1 | Nos. |  | 0
7 |  | IR High accuracy High sensitivity (110 V/W) Low resistance (50 KΩ) and therefore Very good signal-to-noise-ratio Good response time (40 ms) Low cost thin film technology Connectivity sensor | 2 | Nos. |  | 0
8 |  | 6 white–color, touch–sensitive buttons Custom labeled, removable button caps 1 Ethernet port 1 KNET™ port 2 Bidirectional RS–232 ports 2 IR emitter ports 3 Relay ports 1 IR sensor for learning Site–CTRL software compatible Mounts in standard 1 gang US wall junction boxes | 2 | Nos. |  | 0
9 |  | Liquid Retina display 21.08 cm / 8.3-inch (diagonal) LED-backlit Multi-Touch display with IPS technology 2266x1488 resolution at 326 pixels per inch (ppi) Wide colour display (P3) True Tone display Fingerprint-resistant oleophobic coating Fully laminated display Anti-reflective coating 1.8% reflectivity 500 nits brightness | 1 | Nos. |  | 0
10 |  | 8 Channel - High Power (230v) relay. • Controlling Motors for up/down screen •Projector Mounting Kit up/down •Curtains open/close •Power ON the projector / switcher in sequence •Power ON/OFF the lights | 1 | Nos. |  | 0
11 |  | DIN Rail 0-10V Dimmer Module, 4 feeds, 4 channels. Input Power •230 V~ (CE) 50 Hz •Lightning Strike Protection: Can withstand voltage surges of up to 6000 V~ and current surges up to 3000 A. 4 preset lighting scenes and off are accessible from the Control Unit front panel. •12 additional scenes are stored in the Control Unit. These scenes are accessible via Wallstations and/or Control Interfaces. •Light levels fade smoothly between scenes. Fade time can be set differently for each scene, between 0-59 sec. or 1-60 min. Fade time from Off is capped at 5 sec | 1 | Nos. |  | 0
|  | EXECUTIVE AREA, WAITING AREA, AGM & DGM Rooms |  |  |  | 0
1 |  | Camera Video Resolution : 4K/30, 1080P/30, 720P/30 etc Sensor : 1/2.5 inches, CMOS, Effective Pixels: 8.51 Megapixels Lens :121° (DFOV), 110° (HFOV), 75° (VFOV), 5x zoom, pan/tilt ±15° PTZ : Mechanical PTZ (MPT) + e- PTZ (EPTZ) Digital Noise Reduction : 2D&3D digital noise reduction Video S/N : ≥55dB Backlight Compensation : Support Audio Minimum number of Mic : 4 Mics Frequency Range : 100Hz – 16KHz Full frequency speaker : 96 dB SPL at 0.5 meter Microphone array : Beamforming microphone, pick up distance up to 6 meters External MIC : Support（Optional ) Speaker Out put : 5 Watts or more USB Featured - Connection type : USB 3.0，downward compatible with USB2.0 Color System / Compression : H.264 / MJPEG /YUY2 /NV12 USB audio : 32K sampling rate, support UAC1.0 USB video communication protocol : UVC 1.1~1.5 ,UVC PTZ Protocol : Support ,Input/output interface HD output : 1 * HDMI , version 2.0 ; Audio Interface : 1 * RJ45: D-MIC Input ; （Optional） USB interface, : 1 * USB3.0, Type C ; 1 * USB2.0, Type A ; Wireless : Bluetooth data communication ( Optional) System Compatibility OS - Windows 7 (only 1080p and below), Windows 8.1, Windows 10 or higher, macOS®10.10or higher, Google ChromebookTM Version 29.0.1547.70 or higher, Linux (requires support for UVC), Android Hardware platform: 2.4 GHz Intel® Core 2 Duo processor or higher 2 GB of memory or higher USB 2.0 interface (4K video output need USB 3.0 interface) | 8 | Nos |  | 0
2 |  | Supply, installation, testing & Commissioning of 43 inch 4K (3,840 x 2,160), Professional Slim Blade Stand Display with 4K HDR Processor X1,HDR (HDR10, HLG, Dolby Vision), Direct LED, Dynamic ,Birghtness 440nits , contrast ratio upto 400,000:1,4K X-Reality PRO,TRILUMINOS PRO technology, 24/7 Portrait ,Tilt functionality, Flexible Content Layout with HTML5, 16GB On Board Storage, Motionflow XR,HDCP 2.3 (HDMI) / RS232 / USB / RJ45 / Wi-Fi with In-Built Bluetooth / 20W Speakers / Android™ OS system, Viewing angle 178 degree, Pro Mode, Pro Display using Apple AirPlay & Chromecast, Good quality/ OEM frame /bracket for 43" display solid panel complete in all respect with required accesories as desired by Engineer- In- Charge. | 12 | Nos. |  | 0
Out Door LED | [5 empty] | 0
1 |  | VideoWall Screen Size of LED Screen 21 X 9 ft Display Size (W x H) - 4800 mm x 2880 mm or higher Pixel Pitch - 6.67 mm or better (Lower pitch is regarded as better) LED Configuration - RGB 3 in 1 SMD Pixel Density - Minimum 22,500 pixels per sqm or higher Viewing Angle - H 140 degrees / V 120 degrees or better Refresh Rate - >3840 Hz or better LED Makes - Nichia/Cree/Osram/Nationstar Temp Range - -20 to +50 Degrees C or better Grey Scale Processing - 14 Bit or better Brightness (Calibrated) - 5000 cd/m² or better Maximum Power Consumption - 900 w/sqm or lower Dimming Capability - 255 levels Power Input - 200 ~ 240 VAC Individual Tile/Cabinet Dimensions - 960 mm (W) x 960 mm (H).x 92 mm (D) Lower depth will be acceptable , Cabinet Material - Aluminum, Contrast Ratio - 5000:1 or Higher Scan - 10s or better, Auto Brightness - Auto Brightness Sensor to be provided Access for Maintenance - Rear or Front Ingress Protection of Front of Tile - Should meet or exceed Front IP65 . - Ingress Protection Rear of Tile - Should meet or exceed Rear. Safety Certifications (Mandatory to submit along with the bid) - BIS Registration (Bureau of Indian Standards) As per Standard: IS 13252(PART 1) :2010 Quality/Health & Safety/Environmental Certifications of OEM/OEM subsidiary in India (Copy to be submitted along with the bid - Quality Management System 9001:2015, - Occupation health & Safety Management System - OHSAS 18001:2007, - ISO 27000:1- Environmental Management System 14001: 2015. | 1 | 3100000 |  | 0
2 |  | POWER DISTTRIBUTION UNIT --- An IP 54 rack shall be provided to house the various components required to drive the Outdoor LED wall. - Front Door - 2 Hinges with Rack & Aircon bolted Wall Mount Clamp - Welded on Rack frame rear side 19" pillar front & 19" pillar rear - Bolted on rack side wall Locking Arrangement - To be provided with a locking system Limit Switch - The rack door to be provided with a limit switch Earthing - Earthing studs should be provided in the rack for earthing purposes Cable points - Cable entry and exit points should be provided in the rack Mounting - Should be possible to mount the rack either on a pole or on a wall with options of different mounting types Material - GI 120 gsm thickness 1.5 mm IP rating - IP54 AC input - 380V/220V AC Power Load Max - 5KW Surge protection - Class C Over temperature protection - Selectable from 30 deg. to 60 deg. C A | 1 | Nos. |  | 0
3 |  | Controller Unit --- Control Port - RS232 or LAN Signal Input - DVI/HDMI Minimum Load Capacity - 497664 Pixels Input Voltage - 100~240 VAC Operating Temperature - 5~40 Deg. C | 1 | Nos. |  | 0
|  | SURVEILLANCE CONTROL RROM |  |  |  | 0
1 |  | 3x2 60" 4KDLP-Laser Video Wall with 0.2mm bazel :- VIDEO WALL CUBES OF 60" DIAGONAL IN A SUITABLE CONFIGURATION WITH TOTAL VIDEO WALL NATIVE RESOLUTION 11520 X 4320 PIXELS COMPLETE WITH BASE STANDS including with Cube & Controller: Cube & controller should be from the same manufacturer , The OEM should be an established multinational in the field of video walls and should have installations around the world , Total Video Wall Resolution:11520 x 4320 pixels or higher,Laser light source, Brightness Uniformity: ≥ 95 % ,Dynamic Contrast:1000000:1 or more,IP based control to be provided,IR remote control should be provided for quick access,Screen to Screen Gap: ≤ 0.2 mm at 22~ 25 ° C ( control room Temperature ),Screen should be minimum 3 layers with a Hard Backing to prevent bulging ,Half viewing angles of H : ±36° and V : ±34°,Input: 1 x HDMI 2.0,Input: 1 x Dsub-15 ,Input: 1 x Display port 1.2,Cube should be equipped with a built in dual redundant power supply built inside the cube,By Means of a heat pipe . No hazadrous liquid to be used inside the cooling system. OEM to declare the liquid being used in the cooling system.,IP6X certification from a third party lab to be provided as proof of meeting the parameter,Total Cube depth should be equal or less than 500 mm,System should able to switch to secondary input if primary input is not available,System should also automatically switch back to primary input from secondary input as soon as the primary input is available again.,Monitoring of critical parameters :Internal Temperature,Brightness ,Cooling ,Light Source Status,Should be possible to demonstrate these parameter through active monitoring interface,Maintenance Access is rear,Each cube should have a screen size of 1328 mm wide and 747 mm high,Videowall should be equipped with a cube control & monitoring system,System should be based on Python- Django framework with web browser architecture ,Should be able to control & monitor individual cube , multiple cubes and multiple video walls ,Provide videowall status including Source , light source ,temperature, fan and power information ,Should provide a virtual remote on the screen to control the videowall,Input sources can be scheduled in " daily", "periodically" or "sequentially" mode per user convenience,System should have a quick monitor area to access critical functions of the videowall,User should be able to add or delete critical functions from quick monitor area ,Automatically launch alerts, warnings, error popup windows in case there is an error in the system ,User should be able to define the error messages as informational, serious or warning messages,Automatically notify the error to the administrator or user through a pop up window and email ,Status log file should be downloadable in CSV | 1 | Nos. |  | 0
2 |  | Controller to control video wall with 10 inputs and 10 output and wall management software. |  |  |  | 0
|  | CCTV Infra BOQ |  |  |  | 0
1 |  | 2 MP IP FIXED LENS DOME CAMERA: Supply, Installation, Testing & Commissioning of 2MP Mini Dome Camera, True Day Night camera with IR Illuminator, 1/3” 2 Megapixel progressive scan CMOS, 30FPS@1920x1080 (2MP), True WDR, 120dB, Triple streams, Wide Angle Fixed lens 2.8 mm , BLC, 3DNR, inbuilt Motion Detection & Tampering detection , Auto White Balance, Privacy Mask, high power LEDs IR with upto 30m IR distance, Min 256GB SD Card Slot provision, PoE, H.265, H.264 and MJPEG, IEEE 802.3af PoE Class 2, IP 66 & IK10 Having Operating temp range : –30°C to 55° C, Embedded Cyber Security, NDAA Compliant, ONVIF compliant, UL, BIS | 100 | Nos |  | 0
2 |  | 2 MP IP VF DOME CAMERA: Supply, Installation, Testing & Commissioning of 2MP Mini Dome Camera, True Day Night camera with IR Illuminator, 1/3” 2 Megapixel progressive scan CMOS, 1920x1080 (2MP), P Iris, AGC - Auto/Manual, WDR, 120dB, Triple streams, Varifocal lens 2.7 - 13.5mm, Remote Focus, BLC, 3DNR, Edge Analytics: Intrusion detection, loitering detection, line crossing detection, face detection, crowd/ running detection, missing/ unattended object detection, Motion Detection & Tampering detection , Auto White Balance, Privacy Mask, high power LEDs IR with upto 30m IR distance, Two Way Audio - G.711, G.726, Min 256GB SD Card Slot provision, Ausio In, PoE, H.265, H.264 and MJPEG, IEEE 802.3af PoE Class 0, IP 66 & IK10 Having Operating temp range : –30°C to 55° C, Embedded Cyber Security, NDAA Compliant, ONVIF compliant, UL, BIS | 15 | Nos |  | 0
3 |  | 2 MP IP FIXED LENS Bullet CAMERA: Supply, Installation, Testing & Commissioning of 2MP Mini Bullet Camera, True Day Night camera with IR Illuminator, 1/3” 2 Megapixel progressive scan CMOS, 30FPS@1920x1080 (2MP), True WDR, 120dB, Triple streams, Wide Angle Fixed lens 2.8 mm , BLC, 3DNR, inbuilt Motion Detection & Tampering detection , Auto White Balance, Privacy Mask, high power LEDs IR with upto 30m IR distance, Min 256GB SD Card Slot provision, PoE, H.265, H.264 and MJPEG, IEEE 802.3af PoE Class 2, IP 66 & IK10 Having Operating temp range : –30°C to 55° C, Embedded Cyber Security, NDAA Compliant, ONVIF compliant, UL, BIS | 5 | Nos |  | 0
4 |  | Supply, Installation, Testing & Commissioning of 32 Channel Network Video Recorder : Embedded OS Linux, CPU ARM Processor, Flash 256 MB, RAM 4 GB, Watchdog Hardware + Software, Power Restoration System Restart Automatically after Power Recovery, Record Throughput (MB) 192 Mbps, Network Throughput (MB) min 200 Mbps, HDD Devices Internal x 4, supports RAID 0, 1, 5 (RAID Max. Volume: 16TB), Video Output HDMI x 1, VGA x 1, support H.265, H.264, MPEG4 and MJPEG Multiple codec. Up to 20 MP camera supported, USB Interface Front: 2 (USB 2.0) Back : 1 (USB 3.0) Alarm In 16, Alarm Out 8, Audio 3.5 Phone Jack Audio Output x 1, 3.5 Phone Jack Audio Input (Reserved) x 1, RS485 1 Port (Reserved), Network Interface 10/100/1000Mbps, Ethernet (RJ-45) x 2, PoE 16x 802.3at/af Compliant PoE Ports, (Total Max. 160W), Motion Detection, Smart VCA Ev ent, Cy ber Attack, PIR Detection, Tampering Detection, Camera DI/DO, Camera Disconnected, Disk Failure, Disk Full, NVR DI/DO,PoE error, Fan error etc Protocols IPv 4, IPv 6, TCP/IP, HTTP, HTTPS, UPnP, RTSP/RTP/RTCP, SMTP, FTP, DHCP, NTP, DNS, DDNS, IP Filter Power Safety Certifications UL, BIS. Recording @ H.265 Compression, 1080P/25FPS/Motion Based recording/45 days. | 4 | Nos |  | 0
5 |  | 16 Port Giga POE Switches. | 7 | Nos |  | 0
6 |  | 24 Port Giga POE Switches. | 2 | Nos |  | 0
7 |  | 128 Channel NVR with RAID. | 1 | Nos |  | 0
8 |  | 12TB Surveillance Hard Disks | 16 | Nos |  | 0
9 |  | 30U Server Rack with Patch Panels Approved makes - | 1 | Nos |  | 0
10 |  | Installation of Cat6 Cable with Conduit. Approved makes | 6000 | Mtrs |  | 0
11 |  | Supply and Installation of -10 mm Pixel Pitch based Outdoor Direct View True Color LED Wall inclusive of LED control system & PDU with 2 years warranty *Size : 6feet X 8feet and Resolution 672 x 288 | 1 | Nos. |  | 0
|  | SOLAR PV COSTING CALCULATION ACCORDING TO TERRACE AREA AVAILABLE |  |  |  | 0
1 |  | Supplying and erecting, testing and commissioning solar pv System suitable for hot and dry weather with solar panelwith all necessary arrangement complete. Solar on Grid , Mono crystallinr pv module ; 545Wp/540Wp Mono perk Half Cut. Approved Makes - Adani / Tata / Vikram 535+ Monocrystalline Modules, with Material Warranty 10 years & Performance warranty up to 25 years of Efficiency 20.23- 21.2% 1 x 30 Kw As per final design Efficiency-98% or above, with Warranty upto 10 years with all necessary protections IP 68 Approved Make : Delta ¦ Growatt ¦ Schneider Certified For Applications With Modules According To IEC 61730, Safety Class II, Certified For Applications With Modules According To IEC 61730, Safety Class II, 1C 4 SQ MM TUV Standard for DC and AC cable as per design Resistance against UV, Water, Ozone, Fluids, Oil, Salt & General Weathering. Annealed tinned flexible copper conductor 3 phase, 415 V Enclosure MCCB/MCB, AC SPD, RYB Phase indication with accessories IP 68 Enclosure All Switchgear L&T/Schneider /Siemen Online Portal with data logger Compatible to Inverter ,Lighting Arrestor25 Mtr Radius, IEC 62305 Standard Danger boards where necessary as per IE Act. /IE Rules as amended up to date. Cable Tray 1.6 Hot Dip GI perforated cable trays with cover and Jointing plates Earthing Maintenance free Chemical Earthing with Earthing electrode & Earth pit cover SGI 3 Nos NET METERING as per the maharashtra state renewable energy | 35 | Per KWP |  | 0
|  | IT Infra BOQ |  |  |  | 0
1 |  | Providing and fixing FAN ICX 7450 exhaust airflow fan, front to back airflow (two fans required when using two power supplies) | 3 | Nos. |  | 0
2 |  | Providing and fixing ICX7450/6610/6650 NON-POE 250W AC PSU, exhause airflow, front to back airflow | 3 | Nos. |  | 0
3 |  | I/O plates with Modules (LAN Points with redudancy) | 200 | Nos |  | 0
4 |  | Patchcords of lengths (1/1.5/3 Mtrs) | 1000 | Nos |  | 0
5 |  | 6U Network Racks with Patch Panel | 8 | Nos |  | 0
6 |  | 30U Server Rack with Patch Panels | 2 | Nos |  | 0
7 |  | 48 Port Gigabit LAN Switch | 6 | Nos |  | 0
8 |  | 48 Port 10G Core Switch | 1 | Nos |  | 0
9 |  | Firewall for Internet | 1 | Nos |  | 0
10 |  | Installation of Cat6 Cable with Conduit | 12000 | Mtrs |  | 0
11 |  | WIFI Ceiling Mount Access Point devices | 24 | Nos |  | 0
12 |  | WIFI Access Point Controller | 1 | Nos |  | 0
13 |  | Network multifunction Printer / copier (Monochrome) | 4 | Nos |  | 0
|  | Infra for PA System |  |  |  | 0
1 |  | SITC of 6.5-inch, 2 way, Ceiling-mount loudspeaker. Low-saturation 70V/100V transformers with 8-ohm bypass,Frequency Range-65 Hz – 20 kHz, Rated noise power / voltage-30 watts / 15.5 volts (rms), Sensitivity-89 dB SPL, Coverage- 110° conical (500 Hz to 5 kHz), Maximum continuous SPL-96 dB, Maximum peak SPL- 110 dB, LF Transducer - 6.5-inch Polypropylene cone with butyl rubber surround, HF Transducer - .86-inch silk dome tweeter, coaxially mounted. Rated impedance- 8Ω, Transformer Taps 70 V: 30, 15, 7.5, 3.7, 1.9 watts, 100V: 30, 15, 7.5, 3.8, watts | 30 | Nos |  | 0
2 |  | SITC of Page Station with 16 Buttons command keypad and Gooseneck mic.Capacitive touch, programmable keypad and 240 x 64 graphics LCD for flexible customization,Second microphone input and GPIO allow one Page Station to serve two locations,Dual Ethernet connections support network redundancy,Audio Channels-2 line inputs, 1 line output,Power-IEEE 802.3af power over Ethernet (POE) or +24V DC,Frequency Response- 20 Hz - 20 kHz (max)-± 0.5 dB,20 Hz - 20 kHz (typical)- ± 0.2 dB, Input Impedance(Balanced/Unbalanced)-10k ohms | 1 | Nos |  | 0
3 |  | SITC of 4-Channel Network based amplifiers with 5th Generation Class D hybrid powertrain design. 350W/CH @ 16, 700W/CH @ 8, 800W/CH @4 & 600W/CH @2 Ohms & 700W/CH @ 100v/70v Tapping. 2 Channels Bridge Mode: 1500W/CH@ 8 &4 Ohms & 200v/1400v Tapping. 4 Routable Mic/ Line Inputs with 12V Phantom Power. Power Sharing between 2 channels feature for wattage distribution as per the load required by speakers in respective areas. Control & Monitoring: Centralised Processor over IP. GPIO: Eight configurable, bi-directional GPIO connections, Frequency Response: 20 Hz - 20 kHz +0.2 dB / -0.7 dB. Input Impedance: >8k balanced and >4k unbalanced. Controls & Indicators: Power, Channel MUTE buttons, Channel SELECT buttons, Channel Input signal and CLIP LED Indicators, Channel Output and LIMIT LED meters, NEXT, PREV, ID buttons, Control knob, LCD Graphic Display. | 1 | Nos |  | 0
|  | SITC of Digital Signal Processor with 8 mic/line level analog audio inputs, 8 line level analog audio outputs, 8 Flex Channel mic/line level analog audio inputs or outputs, Up to 16 assignable and routeable AEC processor instances, 16 General Purpose Inputs (GPI) x16 General Purpose Outputs (GPO), Input Frequency Response-20Hz to 20kHz @ +21dBu,Input Impedance (balanced)-5K Ohms Nominal, Input Sensitivity Range (1dB Steps)--39 dBu min to +21 dBu max, A/D – D/A Converters - 24-bit, Sampling Rate-48kHz, Input Impedance (balanced)-5K ohms nominal, Output Dynamic Range-> 108dB,Inbuilt 16 Multitrack Player capacity,Front Panel monochrome OLED with capacitive touch buttons for settings. Control and integrate external devices using TCP/IP, RS232 and GPIO. | 1 | Nos |  | 0
|  | SITC of User Control Interface Deployment Software License for above mentioned Digital Signal processor, Should be Perpetual and installed on DSP processor. Should support multiple User Control Interfaces simulataneously | 1 | Nos |  | 0
|  | SITC of User Control Interface Deployment Software License for above mentioned Digital Signal processor, Should be Perpetual and installed on DSP processor. Should support control of multiple devices simutaneously via Ethernet, RS232 and IR. | 1 | Nos |  | 0
|  | SITC of TableTop Touch Controller with Capacitive Touch Surface, In-Plane Switching (IPS) technology, 16M colors. Viewable Screen. Dimensions: 8", Resolution: 1280 x 800, Brightness: 4000 Nits. Panel Orientation: Vertical/ Horizontal, Operating Temperature: 0°-50° C, Rear Panel Connectors: LAN, 1000Mbps full-duplex RJ-45 L. POE: IEEE PoE 802.3af class 3 via LAN port. Configurable over the layer 3 network to the remote DSP via Network Switch | 1 | Nos |  | 0
|  | SITC of Hardware Connector | 2 | Nos |  | 0
|  | SITC of Speaker 2 Pair cable | 2000 | RMT |  | 0
|  | Infra for Access Control and Attendance System |  |  |  | 0
1 |  | Baggage Scanner Net Weight: 500 kg. Conveyor Speed: 0.20 m/sec. Monitor type: LCD. Energy Imaging: 4-6 Colours. Zoom Real Time: 64 X. Image Archiving: 100,000 min. | 1 | Nos |  | 0
|  | Infra for EPABX (Intercom) |  |  |  | 0
1 |  | 128 Port EPABX System (Hybrid Analog+Digital) | 1 | Nos |  | 0
2 |  | MDF / Distribution Boxes with Krones Weather resistant Quality tested FIRE RESISTANT | 8 | Nos |  | 0
3 |  | Standard Telephone Instruments | 110 | Nos |  | 0
4 |  | IP Phone Instruments | 10 | Nos |  | 0
5 |  | Cabling for Intercom System | 6000 | Mtrs |  | 0
|  | UPS BOQ |  |  |  | 0
1 |  | 15KVA Single Phase online UPS with 1 Hrs Backup | 5 | Nos |  | 0
2 |  | 5KVA Single Phase online UPS with 4 Hrs Backup | 6 | Nos |  | 0
3 |  | UPS related electrical cabling | 300 | Mtrs |  | 0
|  | WIFI |  |  |  | 0
1 |  | R610 dual-band 802.11abgn/ac (802.11ac Wave 2) Wireless Access Point, 3x3:3 streams, MU-MIMO, BeamFlex+, dual ports, 802.3af/at PoE support. Does not include power adapter or PoE injector. Includes Limited Lifetime Warranty. | 2 | Nos |  | 0
2 |  | R310 dual-band 802.11abgn/ac (802.11ac Wave 2), Wireless Access Point, 2x2:2 streams, MU-MIMO, BeamFlex+, dual ports, 802.3af PoE support. Does not include power adapter or PoE injector. Includes Limited Lifetime Warranty. | 2 | Nos |  | 0
3 |  | R510 dual-band 802.11abgn/ac (802.11ac Wave 2), Wireless Access Point, 2x2:2 streams, MU-MIMO, BeamFlex+, dual ports, 802.3af PoE support. Does not include power adapter or PoE injector. Includes Limited Lifetime Warranty. | 2 | Nos |  | 0
4 |  | T300 dual-band 802.11abgn/ac (802.11ac Wave 2), Wireless Access Point, 2x2:2 streams, MU-MIMO, BeamFlex+, dual ports, 802.3af PoE support. Does not include power adapter or PoE injector. | 4 | Nos |  | 0
5 |  | Partner support for T300, 5 years | 2 | Nos |  | 0
6 |  | R710 dual-band 802.11abgn/ac (802.11ac Wave 2), Wireless Access Point, 4x4:4 streams, MU-MIMO, BeamFlex+, dual ports, 802.3af/at PoE support. Does not include power adapter or PoE injector. Includes Limited Lifetime Warranty. | 2 | Nos |  | 0
7 |  | Secure Mounting Bracket for Ruckus R720, R710. Mounts to hard wall/ceiling, pole, and truss. Also fits R500, R510, R610, R600, R310, M510 and R700 without pad-lock support. | 10 | Nos |  | 0
8 |  | SmartZone 100 with 2x10GigE and 4 GigE ports, 90-day temporary access to licenses. | 1 | Nos |  | 0
9 |  | AP management license for SZ-100/vSZ 3.X/SCG200/SZ300, 1 Ruckus AP access point. Order this when you intend to run software version from 3.2 onwards. | 5 | Nos |  | 0
10 |  | Partner WatchDog Support Per SZ/vSZ AP, 5 YR | 5 | Nos |  | 0
11 |  | Partner WatchDog Support for SmartZone 100 with 2x10GigE and 4 GigE ports, 5 Year | 1 | Nos |  | 0
|  | INTEGRATED BUILDING MANAGEMENT SYSTEM |  |  |  | 0
A |  | CENTRAL CONTROL STATIONS FOR IBMS SYSTEM |  |  |  | 0
|  | Supplying, Installing, Testing & Commissioning of the Central Control Stations consisting of the following |  |  |  | 0
1 |  | BMS SERVER / CLIENT WORK STATION / PRINTER |  |  |  | 0
1.1 |  | Server for BMS software BMS Computer System: Supply, installation, testing and commissioning of I7 Processor or Equivalent Server PC, 4MB Cache with 8 GB RAM, & 1 TB HDD, 10/100 Mbps Ethernet card, USB connection & internal modem, Microsoft(R) Windows(R) 8 or better or latest OS Professional Enterprise, Web server software, DVD-ROM Drive (with RAM), 100/1000 Mbps NIC for Network connection and anti virus software with 21" colour graphics monitor as per Tender Specifications. Accessories included Optical Mouse, Key Pad, with the above BMS System configuration. | 1 | No. |  | 0
2 |  | BMS SOFTWARES / ENERGY MANAGEMENT |  |  |  | 0
|  | Supply, installation, testing & commissioning of the following Software for BAS: |  |  |  | 0
2.1 |  | BUILDING MANAGEMENT SYSTEM WEB-BASED SERVER SOFTWARE & Energy management System BMS System Software : Supply, installation, testing and commissioning of the simultaneous minimum 5 user Web Based Graphical Software meeting the requirements in the Given I/O Summary and technical specifications including configuration and facility to create / provide the graphic mapping for all I/O Summary points , animate the Graphics, Navigation between pages, display of logs, changing the time zones, popup alarms, configurable password protection for Building Management System as per Technical Specifications. Software shall be able to communicate with open protocols like BACNet/OPC devices simultaneously. | 1 | No. |  | 0
0
3 |  | IP BASED 3rd PARTY INTEGRATOR |  |  |  | 0
|  | SYSTEM INTEGRATION UNITS FOR 3RD PARTY SYSTEM SOFTWARE INTEGRATION - UL listed Controllers. Supply, installation, testing and commissioning of Bacnet IP/Lonmark IP852 (open Protocols) Integration units, to connect individual 3rd party microprocessor system controllers like energy Meters , Fires alarm System , IAQ Sensor etc. the unit shall be capable of integrating all mentioned devices on BACnet, Modbus & LON etc.Integrator Should be Same OEM Manufacturing 3rd Party Integrator Strictly not Allowed, Each Integrators should be UL & BTL Approved & Certified. | 1 | Lot |  | 0
3.01 |  | Developing and commissioning of software interface for VRV ODU's - Max 600 Points - 8ODU & 33IDU | 1 | Lot |  | 0
3.02 |  | Developing and commissioning of software interface for FAS system - Max 600 Points | 1 | Lot |  | 0
3.03 |  | Developing and commissioning of software interface for Energy Meters - max 12 nos. | 1 | Lot |  | 0
3.04 |  | Developing and commissioning of software interface for UPS - Max 20 Points | 1 | Lot |  | 0
0
0
4 |  | IP BASED CONTROLLERS |  |  |  | 0
|  | DDC Panel inclusive of DDC Controllers PROGRAMMABLE & APPLICATION SPECIFIC CONTROLLER (DDC) - Supply, installation, testing and commissioning of Bacnet IP/Lonmark IP852 (open Protocols) Direct Digital Controllers, The networkable controllers shall be , UL and BTL/Lonmark IP852 certified, vendor shall submit BTL/Lonmark IP852 certificate along with bid) with 32 bit microprocessor, real time clock & programmable memory. The Controller shall have built-in two Ethernet ports. preferably Each DDC and IO module shall have built in LCD display & dial/button for local control & monitoring. The networkable DDC's shall be capable of peer to peer communication with lockable IP65 rated MS mounting cabinets duly powder coated connector strip, internal wiring and space to house controller & relays, connector etc. as per IO Summary. The Controller shall have built in memory to save graphics & logis for the connected points. The controller shall have minimum 20% spare IO capacity. Each Controllers should be UL & BTL Approved & Certified. |  |  |  | 0
4.01 |  | Basement II | 1 | Lot |  | 0
4.05 |  | 3rd Floor | 1 | Lot |  | 0
4.08 |  | Terrace | 1 | Lot |  | 0
0
5 |  | SENSORS & FIELD DEVICES |  |  |  | 0
|  | Supply, Installation & Commissioning of following equipment for BAS |  |  |  | 0
5.01 |  | Indoor Quality Sensor Indoor Quality Sensor - should include , Carbon Dioxide (CO2),Fine Suspended Particulates (PM2.5), and Suspended Particulates ( PM10) Total Volatile Organic Compounds (TVOC) and Temperature, Humidity, with inbuilt display and alarms | 9 | Nos. |  | 0
5.02 |  | CO Sensor | 4 | Nos. |  | 0
5.02 |  | Bi- Level Switches for Water Tank | 10 | Nos. |  | 0
0
8 |  | CABLES & ACCESSORIES FOR BAS |  |  |  | 0
8.1 |  | Supplying, installing, testing and commissioning of 2 Core X 1.0 Sqmm Shielded Armoured FRLS Copper Cable (per I/O points hard wired to DDC). | 1500 | MTRS |  | 0
8.2 |  | Supplying, installing, testing and commissioning of 4 Core X 1.5 Sqmm Shielded Armoured FRLS Copper Cable (per I/O points hard wired to DDC). | 2000 | MTRS |  | 0
8.4 |  | Supplying, installing, testing and commissioning of 3 Core X 1.5 Sqmm Armoured Cable (per DDC to UPS Power Supply). | 150 | MTRS |  | 0
8.5 |  | Supplying, installing, testing and commissioning of CAT-6 Armoured Cable | 600 | MTRS |  | 0
|  | FURNITURE WORK |  |  |  | 0
1 |  | Facade of Entrance Door | 160 | SQ.M |  | 0
|  | Supply, fixing and installation of 4mm thick Aluminium Composite Panel (ACP) of approved colour for external cladding in combination of solid and metallic colours, including all necessary Framework, support and complete weather sealing as per architectural drawing. The Aluminium Composite Panel (ACP) should be made out of thermoplastic core of low-density polyethylene LDPE (100% virgin mix), sandwiched between two aluminium sheets of ALLOY GRADE- 5000 series, each not less than 0.50 mm thick, total thickness of aluminium composite panels not to be less than 4 mm, the exposed surface thereof shall have Stove lacquered finishing coat not less than (26 + - 2) micron (containing minimum 70% kynar 500 based PVDF) of colour and shade as per architectural design. The inside surface (facing the building exterior surface)shall have polyster based powder coating not less than 25 Micron with protective peel-off foil on the exterior face (peel off film will in no case leave any adhesive mark over the composite panel surface after it is peeled off). The supporting framework shall be made out of 50 mm X25mm X 3mm thick Aluminium section to be spaced horizontally and vertically for fixing of panel of size 900 mm X 1200 mm and fixed to the building structure as per design through 50mm X50mm X5 mm MS angle clamps prefixed to masonry or slab, columns with Hilti make anchor fastener screws. The fixing of panel to be done with the help of VHB tapes and screws and all the sealing of joints to be done with weather sealent Silicon as directed by Engineer-in-charge. (Prior permission of S.E. is necessary before inclusion of this item in estimate) |  |  |  | 0
2 |  | ACP TO COLUMN/STRAIGHT SURFACE | 170 | sft |  | 0
|  | Supply, fixing and installation of 4mm thick Aluminium Composite Panel (ACP) of approved colour for external cladding in combination of solid and metallic colours, including all necessary Framework, support and complete weather sealing as per architectural drawing. The Aluminium Composite Panel (ACP) should be made out of thermoplastic core of low-density polyethylene LDPE (100% virgin mix), sandwiched between two aluminium sheets of ALLOY GRADE- 5000 series, each not less than 0.50 mm thick, total thickness of aluminium composite panels not to be less than 4 mm, the exposed surface thereof shall have Stove lacquered finishing coat not less than (26 + - 2) micron (containing minimum 70% kynar 500 based PVDF) of colour and shade as per architectural design. The inside surface (facing the building exterior surface)shall have polyster based powder coating not less than 25 Micron with protective peel-off foil on the exterior face (peel off film will in no case leave any adhesive mark over the composite panel surface after it is peeled off). The supporting framework shall be made out of 50 mm X25mm X 3mm thick Aluminium section to be spaced horizontally and vertically for fixing of panel of size 900 mm X 1200 mm and fixed to the building structure as per design through 50mm X50mm X5 mm MS angle clamps prefixed to masonry or slab, columns with Hilti make anchor fastener screws. The fixing of panel to be done with the help of VHB tapes and screws and all the sealing of joints to be done with weather sealent Silicon as directed by Engineer-in-charge. (Prior permission of S.E. is necessary before inclusion of this item in estimate) |  |  |  | 0
3 |  | False Ceiling | 1370 | sq.m |  | 0
|  | PRIVIDING AND FIXING ACOUSTICAL FALSE CEILING WITH 0.7 NRC: Sierra Mineral Fibre Acoustical Suspended Ceiling System with 13mm thick Microlook Edge Tiles with 15mm face exposed grid. The tiles shall have smooth laminated salt pepper visual with Humidity Resistance (RH) of 95%, NRC 0.7 (Average value of Absorption Co-efficient readings taken at 250 Hz, 500 Hz, 1000 Hz and 2000 Hz) as per ASTM C423 standard, CAC of 28db as per ASTM E1414, Light Reflectance ≥85% as per ASTM E-1477, Thermal Conductivity λ = 0.037W/mK, Colour Global White, Fire Performance of class A2 s1, d0 according to EN 13501-1 with 13mm Microlook edge and 8mm drop in module size of 600 x 600mm. The scrim on the face of the tile shall be cleanable. The tiles shall be classified as ISO 14644-1 cleanroom class 5. It shall be suitable for Green Building application, with Recycled content of 60%. The tile shall have certifications from GRIHA and GreenPro thereby confirming that it is an environment friendly product. SUSPENSION: The tile shall be laid on 15 mm wide T - section flanges colour global white (matching to tile color) having roll formed double stroke rotary stitching on all T sections i.e. the Main Runner, 1200 mm & 600 mm Cross Tees with a web height of 38mm (all sections). The deflection loading of the system shall be 12.5 kg/m2 (as per standard installation layout mentioned below) and main beam tested as per ASTM C635 (Deflection limit less than L/360) with a deflection loading of 15kg/m. The end details of the cross tee shall be made of pre hardened steel and fixed to the ends of the cross tee to provide double locking between “cross tee to cross tee” and “cross tee to main beam”. All main beam to main beam and cross tee to cross tee connection shall have a pull out strength of more than 100kg. The T Sections shall be made of hot dipped galvanized steel of 90 gsm as per IS 277 (2003) and pre-painted steel with baked polyester paint with 0T bending capability. All border cross tee/main beam shall be levelled using perimeter fill. The Tile & Grid system used together shall carry a 10 year warranty against manufacturing defect and manufacturer shall provide a warranty certificate. The Tile & Grid shall have the manufacturers name embossed/printed on it. The supply shall be backed by a Manufacturing Test Certificate. |  |  |  | 0
4 |  | False Ceiling (Gypsum Board) | 1020 | sq.m |  | 0
|  | Providing and fixing in position Gypsum board false ceiling with 12.5 mm thick Gypsum boards, screwed/fixed to the under structure of suspended G.I. Grid constructed and suspended from the main ceiling consisting of ceiling sections of size 25 x 50 mm maximum center to center distance of 600 milimetre perimeter channel and intermediate channels at maximum center to center distance 1200 milimetre galvanized grid should be fixed to reinforced cement concrete slab. The gypsum board should be fixed to galvanized iron grid with necessary screws. The boards should be taped and filled from underside to give smooth, seamless ceiling. The rate should include necessary additional ceiling sections and intermediate channels. Additional intermediate channels should be fixed to strap hangers for additional support to prevent strapping at every 1200 milimetre item to be completed in all respect including necessary sleeves for ducts finishing of joints cut outs, painting including labour, material, lifts etc. all complete. |  |  |  | 0
5 |  | TOUGHENED GLASS DOOR | 16 | sq.m |  | 0
|  | Providing and fixing Entrance Door (glazed) in 12mm thk toughened glass with pivot and flooring spring Dorma make, SS handle 300mm wide with frost film. all necessary hardware of Stainless Steel finish as approved by the Project Consultant/ Bank complete in all respects. |  |  |  | 0
7 |  | Front Office Counter: | 8.8 | rm |  | 0
|  | Providing and fixing in position Front Office Counter 2’-6” wide as per drawing No.(1-A, 1-B, 1-C , 1-D & 15) comprising of the following complete in all respects:- |  |  |  | 0
|  | i) Working top made with 25mm thick plywood finished with 1mm thick laminate. Outside edge of the working top shall be provided with 1¼”X1” Teak Wood moulding finished with melamine polish. Inside edge will be provided with ½ “x1” T.W. beading patti with melamine finish. |  |  |  | 0
|  | ii)Vertical facia (Apron) made with 18mm thick plywood finished with 1mm thick laminate with 1mm thick groove at the joint of laminates of two different shades. |  |  |  | 0
|  | iii)Vertical drop (horizontal band) shall be provided on the facia below the working top made with 18mm thick plywood finished with 1mm thick laminate with provision for concealed light, 1 mm thick groove shall be provided at the joint of two different shades of laminate. |  |  |  | 0
|  | iv) Glazed partition above working top to be provided with 12mm thick clear glass cut to the standard shape fixed to partition as per fixing details and to boxing with concealed S. S. finished ‘D’ brackets as shown in the drawing. The exposed edges of the glass shall be finished in mirror polish. |  |  |  | 0
|  | v) 3’-10” high Boxing (10”x10”) made with 18 mm thick plywood finished with 1 mm thick laminate including providing and fixing 6 mm thick square frosted glass at a height 3’-2” above finished floor level. |  |  |  | 0
|  | vi) 1’-9” high Boxing (5”x5”) made with 12 mm thick plywood finished with 1 mm thick laminate. |  |  |  | 0
|  | vii) vertical supports made with 18 mm thick plywood finished with white enamel paint. |  |  |  | 0
|  | viii)Telescopic CPU Stand/ ready made Keyboard tray shall be provided of approved model and make. |  |  |  | 0
|  | ix) Footrest made with T.W. member of size 4”X1 ½ “ finished with french polish. |  |  |  | 0
|  | x) Drawer units as per drawing shall be provided with multipurpose Godrej locks in |  |  |  | 0
|  | Each drawer. Facia of drawer unit shall be finished with 1mm thick laminate and all other sides shall be finished with 0.8MM THK laminate. The drawers will be provided with handles (Stainless Steel finish) and channels as per approval of the Project Consultant / Bank. |  |  |  | 0
|  | xi) Boxing as per drawing made with 12mm thick plywood finished with Synthetic enamel paint shall be provided below the table top for electrical conduiting and at the bottom for the LAN cabling/Telephone wire conduiting. |  |  |  | 0
|  | The item to include all necessary hardware and fittings in Stainless Steel finish, lipping to all edges and making provision only for electrical fitting behind the front. Vertical drop and also in the 10”x10” boxing as shown in the drawing. Necessary beadings with melamine polish for fixing the glass are to be provided. |  |  |  | 0
|  | next to cash cabin |  |  |  | 0
|  | next to customer area |  |  |  | 0
8 |  | Cash Counter: | 4.8 | r.m |  | 0
|  | Providing and fixing in position Cash Counter 2’-9” wide as per drawing No.(2-A, 2-B, 2-C, 2-D, 2-E, 2- F) comprising of the following : |  |  |  | 0
|  | i)Working top made with 25mm thick plywood finished with 1mm thick laminate. Outside edge of the working top shall be provided with 1¼”X1” Teak Wood moulding finished with melamine polish. Inside edge will be provided with ½ “x1” T.W. beading patti with melamine polish. |  |  |  | 0
|  | ii)Vertical facia (Apron) made with 18mm thick plywood finished with 1mm thick laminate with 1mm thick groove at the joint of laminates of two different shades. |  |  |  | 0
|  | iii)Vertical drop (horizontal band) shall be provided on the facia below the working top made with 18mm thick plywood finished with 1mm thick laminate with provision for concealed light, 1 mm thick groove shall be provided at the joint of two different shades of laminate. |  |  |  | 0
|  | iv)Glazed partition of 1’-4” height above working top provided with 12mm thick toughened and frosted glass besides non-transparent film from inside fixed to partition as per fixing details and to boxing with concealed S. S. finished ‘D’ brackets as shown in the drawing. The exposed edges of the glass shall be finished in mirror polish. |  |  |  | 0
|  | v)Transaction top shall be provided with 12mm thick toughened glass (partly glazed partly frosted) fixed horizontally with concealed Stainless Steel D bracket. Both exposed edges (inside and outside) shall be moulded and finished in mirror polish. |  |  |  | 0
|  | vi)Glazed partition having height 1’.0” above the transaction top (in facia) shall be provided with 12 mm thick glass (clear) with cut out of 8”x 4” as per drawing. The edges of cut out and the top edge of glass are to be mirror polished and to be fixed to partition as per fixing details and to boxing with concealed S. S. finished ‘D’ brackets as shown in the drawing. |  |  |  | 0
|  | vii)Glazed partition provided with 12mm thick glass (Clear) above the slit to be fixed to partition as per fixing details and to boxing with concealed S. S. finished ‘D’ brackets as shown in the drawing. . The exposed edges shall be finished in mirror polish. |  |  |  | 0
|  | viii) 7’-7” high Boxing (10”x 10”) made with 18mm thick plywood as per drawing with 1-6” horizontal extension at the top including providing and fixing 6 mm thick square frosted glass at a height of 5”-11” above Finished Floor level. |  |  |  | 0
|  | ix) 1’-9” high boxing (5”x 5”) made with 12 mm thick plywood finished with 1 mm thick laminate are to be provided. |  |  |  | 0
|  | x)Telescopic CPU Stand/ ready made Keyboard tray shall be provided of approved model and make. |  |  |  | 0
|  | xi) Footrest made with T.W. member of size 4”X1 ½ “ finished with french polish. |  |  |  | 0
|  | xii) Drawer units as per drawing shall be provided and each drawer should have vertical partitions for keeping the currency notes and multipurpose Godrej locks. Facia of drawer unit shall be finished with 1mm thick laminate and all other sides shall be finished with 0.8MM THK laminate. The drawers will be provided with handles (Stainless Steel finish) and channels as per approval of the Project Consultant / Bank. |  |  |  | 0
|  | xi) Boxing as per drawing made with 12mm thick plywood finished with .8mm thk laminate shall be provided below the table top for electrical conduiting and at the bottom for the LAN cabling/Telephone wire conduiting. |  |  |  | 0
|  | The item to include all necessary hardware and fittings in Stainless Steel finish, lipping to all edges and making provision only for electrical fitting behind the Vertical drop and also in the 10”x10” boxing as shown in the drawing. Necessary beadings with matching melamine polish for fixing the glass are to be provided as per drawing/ as directed. |  |  |  | 0
9 |  | Solid/Glazed Full Height Partition | 969.75 | sq.m |  | 0
|  | Providing & fixing in position solid Full Height Partition in frame work including door in 2’x 2’ grid (horizontally and vertically) comprising of 2”x 1½” aluminum Section with 8 mm thick plywood on both sides finished with 1 mm thick laminates of approved make and colour as shown in drawing no.17. Item to include 2” x 2” alumimum member filled in with wood for door frame fixed to ceiling so as to sgeregate the door from the partition. All exposed T.W. surfaces to be finished in melamine polish of matching laminate colour as directed including all necessary Stainless Steel finish fittings/ hardware, door closers, Yale locks 8mm thk glass with etched film etc. as per list of approved material and as approved by the Project Consultant/ Bank complete in all respects. with door 35mm thk finished in same as that of partition. |  |  |  | 0
|  | (Note: In case of false ceiling, the vertical Aluminum members to be fixed with pucca ceiling but the area of partition payable will be below the false ceiling only). |  |  |  | 0
10 |  | Partly Glazed Partition for Cash Cabins | 35.52 | sq.m |  | 0
|  | Providing and fixing in position 7’-7” high partly glazed partition for Cash Cabins as per drawing nos. (2-A, 2-B, 2-C, 2-D & 2-E) including door drawing no.(12) in frame work at 2’ x 2 ‘ grid (horizontally and vertically) comprising of 2” x 1½” aluminum Section and / or as per frame work shown in the drawings with 6mm plywood on both sides finished with 1 mm thick laminates of approved shade and colour as shown in drawings. Item to include 8 mm thick glass with etching and frosting as per design and 2”x 2” aluminum. member for door sides and glass sides and aluminum door frame to take 8 mm thick glass with etching and frosting. |  |  |  | 0
|  | The door will be provided with T.W. louvers finished in melamine polish of matching laminate colour. The doors are also to be provided with Godrej Night Latch. Two wooden trays are also to be provided as per drawing. Necessary cutouts are to provided in the glass and the edges of the glass cutouts are to be finished in mirror polish. |  |  |  | 0
|  | All exposed T.W. surfaces to be finished in melamine polish of matching laminate colour as directed including all necessary Stainless Steel finish fittings/ hardware, door closers, Godrej locks and wood preservative paint etc. as per list of approved material and as approved by the Project Consultant/ Bank complete in all respects. |  |  |  | 0
11 |  | Partly Glazed Low Height Partition | 130 | sq.m |  | 0
|  | Providing and fixing in position partly glazed low height partition (21/2” thick) in frame work with T.W vertical members at 2’ c/c and 3 horizontal members at equal distance comprising of 2”x 1½” T.W. Section with 6 mm plywood on both sides finished with 1 mm thick laminates of approved make and shade as shown in drawing no.(14) or (3). Item to include 12 mm thick glass (clear/frosted) to be fixed as shown in drawing. The exposed edges of the glass to be finished in mirror polish. T.W runner should be melamine polished in matching colour of laminate etc complete in all respects. |  |  |  | 0
12 |  | Manager’s Table | 1 | each |  | 0
|  | Providing and fixing in position Manager’s Table of size 5'6"x 2'-6" as per drawing no.(6)/ Officer’s Table of size 4’-6” x 2’-3” as per drawing no. (5) including Side Storage (Credenza) by using 25mm thick plywood for top and 18 mm thick plywood for all other horizontal and vertical members. Telescopic CPU Stand/ ready made Keyboard tray shall be provided of approved model and make. Footrest made with T.W. member of size 4”x 1 ½ “ finished with french polish. |  |  |  | 0
|  | Side Storage ( Credenza) as per drawing shall be provided. Facia of Side Storage (Credenza) shall be finished with 1mm thick laminates as shown in the drawing and all other sides shall be finished with 0.8mm laminate. The Side Storage (Credenza) shall be provided with handles (Stainless Steel finish) and channels as per approval of the Project Consultant / Bank. |  |  |  | 0
|  | All exposed plywood surfaces to be finished with 1mm thk. laminate of approved make & shade, and all exposed edges of table top & ply verticals to have 1" x 1/4" T.W.lipping. All exposed T.W. sections to be melamined and internal surfaces to have white enamel paint as directed. Item to include plywood boxing, all necessary hardware and fittings in Stainless Steel finish, lipping to all edges etc. complete in all respects. |  |  |  | 0
11 |  | DGM/AGM table | 7 | per unit |  | 0
|  | Providing and fixing in position Manager’s Table of size 7'x 2'-6" as per drawing no.(6)/ including Side Storage (Credenza) 4' x 1'6" by using 25mm thick plywood for top and 18 mm thick plywood for all other horizontal and vertical members. Telescopic CPU Stand/ ready made Keyboard tray shall be provided of approved model and make. Footrest made with T.W. member of size 4”x 1 ½ “ finished with french polish. |  |  |  | 0
|  | Side Storage ( Credenza) as per drawing shall be provided. Facia of Side Storage (Credenza) shall be finished with selected veneer, it should be polished using PU and laminated as instructed by engineer in charge and as shown in the drawing and all other sides shall be finished with selected veneer, it should be polished using PU and laminated as instructed by engineer in charge. The Side Storage (Credenza) shall be provided with handles (Stainless Steel finish) and channels as per approval of the Project Consultant / Bank. |  |  |  | 0
|  | All exposed plywood surfaces to be finished with with selected veneer, it should be polished using PU and laminated as instructed by engineer in charge of approved make & shade, and all exposed edges of table top & ply verticals to have 1" x 1/4" T.W.lipping. All exposed T.W. sections to be melamined and internal surfaces to have white enamel paint as directed. Item to include plywood boxing, all necessary hardware and fittings in Stainless Steel finish, lipping to all edges etc. complete in all respects. |  |  |  | 0
12 |  | MEETING VC ROOM TABLE: Providing and fixing in position meeting room Table shape, sizes as per the approved design and profile given in the detailed drawing consisting of Table top 25 mm thick to be made of two 18mm+9mm thick plywood covered with 12 mm thick corian top and 1.0mm thick approved laminate at the bottom. The edge of the table top is to be finished with corian moulding at edge .The under structure of the table is to be made of 90x20mm thk MS powder coated frame support for vertical and MS powdercoated frame work for top support with metal box tray for data and power cable provision19 mm thick plywood with 1.0 mm thick laminate, with necessary leveling arrangements. Provision for power track is to be detailed in the drawing.The entire item is to be completed in totality as per the architectural drawing and directions of the Architect. Item to include 2 nos POP UP Boxes for electrical and data management along with alunimum powder coated cable tray box below table surface. Complete | 1 | Per Unit |  | 0
11 |  | MEETING ROOM TABLE | 1 | per unit |  | 0
|  | Providing and fixing in position meeting room Table shape, sizes as per the approved design and profile given in the detailed drawing consisting of Table top 25 mm thick to be made of two 18mm+9mm thick plywood covered with 12 mm thick corian top and 1.0mm thick approved laminate at the bottom. The edge of the table top is to be finished with corian moulding at edge .The under structure of the table is to be made of 90x20mm thk MS powder coated frame support for vertical and MS powdercoated frame work for top support with metal box tray for data and power cable provision19 mm thick plywood with 1.0 mm thick laminate, with necessary leveling arrangements. Provision for power track is to be detailed in the drawing.The entire item is to be completed in totality as per the architectural drawing and directions of the Architect. Item to include 2 nos POP UP Boxes for electrical and data management along with alunimum powder coated cable tray box below table surface. Complete |  |  |  | 0
10 |  | CONFERENCE ROOM TABLE | 1 | per unit |  | 0
|  | Providin & Fixing Conference Room table of size, with pine wood legs finished with PU polish, 18mm boiling waterproof ply top finished with 6mm corian, table should have cut outs for switches and sockets along with HDMI cable of required length |  |  |  | 0
13 |  | Roller Blinds | 197.1 | sq.m |  | 0
|  | Providing and Fixing Rollar Blinds AMI Make or approved make & shade of 38mm round Aluminium channel with Blackout fabric & telting with chain (Ball) system with all necessary fixtures and fitting etc. complete. (Sample to be final by Engineer In-charge prior execution of work) |  |  |  | 0
14 |  | WRITING DESK | 1.5 | sq.m |  | 0
|  | Providing and fixing on site writing desk made in 12mm clear glass with edge crystal polish supported on panelling behing with F brackets the front shall have 10mm thk glass fixed with S.S studs and caps for holding slips/challans. including dust box shown below. As shown on drawing and directed by Architect. Complete. |  |  |  | 0
15 |  | NOTICE BOARD | 20 | sq.m |  | 0
|  | Providing & fixing on site soft board covered with blazer cloth on 12mm ply as base and 50x25 mm T.W. frame finished in polish. |  |  |  | 0
16 |  | SHELF FOR NOTE COUNTING | 1 | each |  | 0
|  | Providing 25mm thk ply shelf finish in 1.0mm laminate for Note counting fixed to wall. (4'x2') |  |  |  | 0
17 |  | WALL PANELLING | 675 | sq.m |  | 0
|  | Providing wall panelling in 12mm ply with 35x35mm frame work at 600x600mm c/c bothways with 1.0MM THK LAMINATE w 10mm thk lipping finished in matching polish Complete. |  |  |  | 0
18 |  | GYPSUM PANELLING | 1 | sq.m |  | 0
|  | Providing wall panelling in 12mm ply with 35x35mm frame work at 600x600mm c/c bothways with tw 10mm thk lipping finished in matching polish Complete. |  |  |  | 0
19 |  | CHEQUE/SUGGESSTION DROP BOX | 2 | no |  | 0
|  | Providing and fixing 450mmx600mm size box with glass front and locking arrangement in 18mm ply finish in laminate inside and outside, with slot on top. Complete. |  |  |  | 0
20 |  | CARPET | 263.07 | Sq.M. |  | 0
|  | Providing & Fixing in position, Carpet more than 800+ gsm, made with100% stain proof fibres of approved make along with 5mm underlay as per Architectural & Acoustical Design & Instructions & Complete in all aspects including all materials labour,finishing etc complete |  |  |  | 0
21 |  | Storage | 107.29 | Sqm |  | 0
|  | Providing and fixing in position Full height Storage / Low Height Storage/ Back Storage(Credenza) as shown in Drg. using M.R. grade commercial Plywood of required thickness finished with 1mm thick laminates as shown inthe drawing and all other sides shall be finished with white enamel paint as detailed therein. The Storage Units shall be provided with handles (Stainless Steel finish) asper approval of the Project Consultant / Bank. All exposed plywood surfaces to be finished with 1mm thk. laminate of approved make & shade and all exposed edges of plywood to have 1" x 1/4" T.W.lipping. All exposed T.W. sections to be melamined in matching colour laminate and internal surfaces to have white enamel paint as directed. Item to include all necessary hardware and fittings in Stainless Steel finish, Godrej multi purpose locks including magnetic ball catcher etc., complete in all respects. |  |  |  | 0
22 |  | Staff Table | 20 | nos |  | 0
|  | Providing and fixing in position Manager’s Table of size 4.5"x 2'-6" as per drawing no.(6)/ Officer’s Table of size 4’-6” x 2’-3” as per drawing no. (5) including Side Storage (Credenza) by using 25mm thick plywood for top and 18 mm thick plywood for all other horizontal and vertical members. Telescopic CPU Stand/ ready made Keyboard tray shall be provided of approved model and make. Footrest made with T.W. member of size 4”x 1 ½ “ finished with french polish. |  |  |  | 0
|  | Side Storage ( Credenza) as per drawing shall be provided. Facia of Side Storage (Credenza) shall be finished with 1mm thick laminates as shown in the drawing and all other sides shall be finished with 0.8mm laminate. The Side Storage (Credenza) shall be provided with handles (Stainless Steel finish) and channels as per approval of the Project Consultant / Bank. |  |  |  | 0
|  | All exposed plywood surfaces to be finished with 1mm thk. laminate of approved make & shade, and all exposed edges of table top & ply verticals to have 1" x 1/4" T.W.lipping. All exposed T.W. sections to be melamined and internal surfaces to have white enamel paint as directed. Item to include plywood boxing, all necessary hardware and fittings in Stainless Steel finish, lipping to all edges etc. complete in all respects. |  |  |  | 0
23 |  | Toughened glass partition: Providing and fixing Entrance glass partition in 12mm thk toughened glass fixed on continious aluminum clip on fop and bottom all necessary hardware of Stainless Steel finish as approved by the Project Consultant/ Bank complete in all respects. | 81 | sq.m |  | 0
20 |  | CENTER TABLE | 5.6 | rmt |  | 0
|  | Providing and fixing in position Center Table of size 3'x 2' as per drawing no. by using 25mm thick plywood for top and 18 mm thick plywood for all other horizontal and vertical members. Telescopic CPU Stand/ ready made Keyboard tray shall be provided of approved model and make. Footrest made with T.W. member of size 4”x 1 ½ “ finished with french polish. |  |  |  | 0
|  | All exposed plywood surfaces to be finished with with selected veneer, it should be polished using PU and laminated as instructed by engineer in charge of approved make & shade, and all exposed edges of table top & ply verticals to have 1" x 1/4" T.W.lipping. All exposed T.W. sections to be melamined and internal surfaces to have white enamel paint as directed. Item to include plywood boxing, all necessary hardware and fittings in Stainless Steel finish, lipping to all edges etc. complete in all respects. |  |  |  | 0
|  | Conference Room TOTAL AMOUNT |  |  |  | 0

## furniture
Item No. | Particulars | Quantity | Unit | Rate (RS.) | Amount ( Rs. )
MODULAR FURNITURE WORK FOR OFFICE AREA
1 | Providing & Fixing Workstation @ 1050w x 600d WITH 3 Dr Metal pedestal + Metal KBPT + CPU trolley -'Providing and placing spine and fin based modular workstation, with partition thickness as 52.4 mm thk and ht - 1200 including powder coated aluminium trims. FIN: out of 22.5 mm thk panel formed out of blocks which are 18 mm thk PLB boards wrapped with laminate or fabric at intermediate level. Top block finished in fabric/white board/clear glass/fabric magnetic and fabric tackable finish. The top split tiles are in a combination of fabric/white board/clear glass and laminate finish. Bottom block is finished in metal/fabric/ laminate finish. END PANEL: 22.8 mm thk end panel is fitted with the main spine of 52.4 mm in the following size 2'0" wide and 4'0" ht. Following finishes are given on intermediate block fabric/DL, bottom block fabric/laminate/DL and top block fabric/DL. 'Providing and placing WISH spine and fin based modular workstation, with partition thickness as 52.4 mm thk and ht - 1200 including powder coated aluminium trims. FIN: out of 22.5 mm thk panel formed out of blocks which are 18 mm thk PLB boards wrapped with laminate or fabric at intermediate level. Top block finished in fabric/white board/clear glass/fabric magnetic and fabric tackable finish. The top split tiles are in a combination of fabric/white board/clear glass and laminate finish. Bottom block is finished in metal/fabric/ laminate finish. Tiles on main spine: Combination of top tiles are fabric magneitc/fabric/fabric tackable/white board/glass writing board/ clear glass tile/ plain metal/ prelam tile. Bottom tiles - Plain metal/ fabric magnetic/fabric/laminated/prelam. SPLIT Tiles on main spine: Combination of two finishes for the top tiles on the user side shall be split fabric magnetic/fabric tackable/white board/prelam/ plain metal along with split fabric magnetic/fabric tackable/white board/prelam/ plain metal. INTERMEDIATE BLOCKS on main spine Intermediate blocks are given in fabric/DL + Fabric/DL finsh. Wire Management through main spine- Wires shall be taken into the system through cable ducts from the junction boxes and it is carried upto the panels through concealed conduits inside the blocks. HALF SCREEN WITH FRAME - at intermediate position between 2 people and at the end above worktop in clear glass/fabric tackble /laminate/white board finsh.at intermediate position between 2 people and at the end above worktop in clear glass/fabric tackble /laminate/white board finsh. Side panels or legs - out of 25 mm thk prelam particle board with flat pvc lipping edge banding considered only on the open end conditions or metal powder coated legs at the end and shared condition. System shall also have 120 mm high powder coated standalone panel legs to give the system an elevated look. Worksurface - out of 25 mm thk prelam particle board with flat pvc lipping edge banding of size as per mentioned sizes. 3 Dr Metal pedestal: FREE STANDING PEDESTAL WITH FLAT METAL FRONT OF SIZE 390W X 435D X 646HT, 3DR = 2 BOX + 1 FILE, CENTRAL LOCKING. 0.8Mm thick CRCA for Body , Shell and Side Stiffners & bottom. 1.2 Mm thick for top and bottom stiffner. Metal front straight Edge. Swiveling non lockable castors mounted below the body shell. Epoxy polyester powder coated to the thickness of 50 microns. Key Board Pull Out Tray ( Metal KBPT): Size – 522 mm W x 405mm - 635mm D X 77mm – 105mm H, Metal Tray - Tray is made of 0.9 mm thick MS Sheet CRCA. (Size: 482(W) x 270(D) x 18(H) MM). CPU trolley - CPU Trolley Width - 230 - 345mm Depth - 226.0mm Height - 180mm Metal Tray - Tray is made of 1.0 mm thick MS CRCA Sheet and Side support is made of 0.8 mm thick MS CRCA Sheet. Castor - Lockable/Non-lockable twin wheel castors are injection molded in Black Nylon, etc. complet as directed and approved by Architect or Engineer In Charge | 1 | Nos. |  | 0
0
2 | Providing & Fixing Workstation @ 1200w x 600d WITH 3 Dr Metal pedestal + Metal KBPT + CPU trolley- 'Providing and placing spine and fin based modular workstation, with partition thickness as 52.4 mm thk and ht - 1200 including powder coated aluminium trims. FIN: out of 22.5 mm thk panel formed out of blocks which are 18 mm thk PLB boards wrapped with laminate or fabric at intermediate level. Top block finished in fabric/white board/clear glass/fabric magnetic and fabric tackable finish. The top split tiles are in a combination of fabric/white board/clear glass and laminate finish. Bottom block is finished in metal/fabric/ laminate finish. END PANEL: 22.8 mm thk end panel is fitted with the main spine of 52.4 mm in the following size 2'0" wide and 4'0" ht. Following finishes are given on intermediate block fabric/DL, bottom block fabric/laminate/DL and top block fabric/DL. 'Providing and placing WISH spine and fin based modular workstation, with partition thickness as 52.4 mm thk and ht - 1200 including powder coated aluminium trims. FIN: out of 22.5 mm thk panel formed out of blocks which are 18 mm thk PLB boards wrapped with laminate or fabric at intermediate level. Top block finished in fabric/white board/clear glass/fabric magnetic and fabric tackable finish. The top split tiles are in a combination of fabric/white board/clear glass and laminate finish. Bottom block is finished in metal/fabric/ laminate finish. Tiles on main spine: Combination of top tiles are fabric magneitc/fabric/fabric tackable/white board/glass writing board/ clear glass tile/ plain metal/ prelam tile. Bottom tiles - Plain metal/ fabric magnetic/fabric/laminated/prelam. SPLIT Tiles on main spine: Combination of two finishes for the top tiles on the user side shall be split fabric magnetic/fabric tackable/white board/prelam/ plain metal along with split fabric magnetic/fabric tackable/white board/prelam/ plain metal. INTERMEDIATE BLOCKS on main spine Intermediate blocks are given in fabric/DL + Fabric/DL finsh. | 1 | Nos. |  | 0
| Wire Management through main spine- Wires shall be taken into the system through cable ducts from the junction boxes and it is carried upto the panels through concealed conduits inside the blocks. HALF SCREEN WITH FRAME - at intermediate position between 2 people and at the end above worktop in clear glass/fabric tackble /laminate/white board finsh.at intermediate position between 2 people and at the end above worktop in clear glass/fabric tackble /laminate/white board finsh. Side panels or legs - out of 25 mm thk prelam particle board with flat pvc lipping edge banding considered only on the open end conditions or metal powder coated legs at the end and shared condition. System shall also have 120 mm high powder coated standalone panel legs to give the system an elevated look. Worksurface - out of 25 mm thk prelam particle board with flat pvc lipping edge banding of size as per mentioned sizes. 3 Dr Metal pedestal: FREE STANDING PEDESTAL WITH FLAT METAL FRONT OF SIZE 390W X 435D X 646HT, 3DR = 2 BOX + 1 FILE, CENTRAL LOCKING. 0.8Mm thick CRCA for Body , Shell and Side Stiffners & bottom. 1.2 Mm thick for top and bottom stiffner. Metal front straight Edge. Swiveling non lockable castors mounted below the body shell. Epoxy polyester powder coated to the thickness of 50 microns. Key Board Pull Out Tray ( Metal KBPT): Size – 522 mm W x 405mm - 635mm D X 77mm – 105mm H, Metal Tray - Tray is made of 0.9 mm thick MS Sheet CRCA. (Size: 482(W) x 270(D) x 18(H) MM). CPU trolley - CPU Trolley Width - 230 - 345mm Depth - 226.0mm Height - 180mm Metal Tray - Tray is made of 1.0 mm thick MS CRCA Sheet and Side support is made of 0.8 mm thick MS CRCA Sheet. Castor - Lockable/Non-lockable twin wheel castors are injection molded in Black Nylon , etc. complet as directed and approved by Architect or Engineer In Charge |  |  |  | 0
3 | Providing & Fixing Workstation @ 1350w x 600d WITH 3 Dr Metal pedestal + Metal KBPT + CPU trolley- 'Providing and placing spine and fin based modular workstation, with partition thickness as 52.4 mm thk and ht - 1200 including powder coated aluminium trims. FIN: out of 22.5 mm thk panel formed out of blocks which are 18 mm thk PLB boards wrapped with laminate or fabric at intermediate level. Top block finished in fabric/white board/clear glass/fabric magnetic and fabric tackable finish. The top split tiles are in a combination of fabric/white board/clear glass and laminate finish. Bottom block is finished in metal/fabric/ laminate finish. END PANEL: 22.8 mm thk end panel is fitted with the main spine of 52.4 mm in the following size 2'0" wide and 4'0" ht. Following finishes are given on intermediate block fabric/DL, bottom block fabric/laminate/DL and top block fabric/DL. 'Providing and placing WISH spine and fin based modular workstation, with partition thickness as 52.4 mm thk and ht - 1200 including powder coated aluminium trims. FIN: out of 22.5 mm thk panel formed out of blocks which are 18 mm thk PLB boards wrapped with laminate or fabric at intermediate level. Top block finished in fabric/white board/clear glass/fabric magnetic and fabric tackable finish. The top split tiles are in a combination of fabric/white board/clear glass and laminate finish. Bottom block is finished in metal/fabric/ laminate finish. Tiles on main spine: Combination of top tiles are fabric magneitc/fabric/fabric tackable/white board/glass writing board/ clear glass tile/ plain metal/ prelam tile. Bottom tiles - Plain metal/ fabric magnetic/fabric/laminated/prelam. SPLIT Tiles on main spine: Combination of two finishes for the top tiles on the user side shall be split fabric magnetic/fabric tackable/white board/prelam/ plain metal along with split fabric magnetic/fabric tackable/white board/prelam/ plain metal. INTERMEDIATE BLOCKS on main spine Intermediate blocks are given in fabric/DL + Fabric/DL finsh. | 44 | Nos. |  | 0
| Wire Management through main spine- Wires shall be taken into the system through cable ducts from the junction boxes and it is carried upto the panels through concealed conduits inside the blocks. HALF SCREEN WITH FRAME - at intermediate position between 2 people and at the end above worktop in clear glass/fabric tackble /laminate/white board finsh.at intermediate position between 2 people and at the end above worktop in clear glass/fabric tackble /laminate/white board finsh. Side panels or legs - out of 25 mm thk prelam particle board with flat pvc lipping edge banding considered only on the open end conditions or metal powder coated legs at the end and shared condition. System shall also have 120 mm high powder coated standalone panel legs to give the system an elevated look. Worksurface - out of 25 mm thk prelam particle board with flat pvc lipping edge banding of size as per mentioned sizes. 3 Dr Metal pedestal: FREE STANDING PEDESTAL WITH FLAT METAL FRONT OF SIZE 390W X 435D X 646HT, 3DR = 2 BOX + 1 FILE, CENTRAL LOCKING. 0.8Mm thick CRCA for Body , Shell and Side Stiffners & bottom. 1.2 Mm thick for top and bottom stiffner. Metal front straight Edge. Swiveling non lockable castors mounted below the body shell. Epoxy polyester powder coated to the thickness of 50 microns. Key Board Pull Out Tray ( Metal KBPT): Size – 522 mm W x 405mm - 635mm D X 77mm – 105mm H, Metal Tray - Tray is made of 0.9 mm thick MS Sheet CRCA. (Size: 482(W) x 270(D) x 18(H) MM). CPU trolley - CPU Trolley Width - 230 - 345mm Depth - 226.0mm Height - 180mm Metal Tray - Tray is made of 1.0 mm thick MS CRCA Sheet and Side support is made of 0.8 mm thick MS CRCA Sheet. Castor - Lockable/Non-lockable twin wheel castors are injection molded in Black Nylon etc. complet as directed and approved by Architect or Engineer In Charge |  |  |  | 0
4 | CUBICAL WORKSTATION :Providing & Fixing Cubical Workstation of size 1350w x 600d + 900w x 450dCUBICAL WORKSTATION-'Providing and placing spine and fin based modular workstation, with partition thickness as 52.4 mm thk and ht - 1200 including powder coated aluminium trims. Tiles on main spine: Combination of top tiles are fabric magneitc/fabric/fabric tackable/white board/glass writing board/ clear glass tile/ plain metal/ prelam tile. Bottom tiles - Plain metal/ fabric magnetic/fabric/laminated/prelam. SPLIT Tiles on main spine: Combination of two finishes for the top tiles on the user side shall be split fabric magnetic/fabric tackable/white board/prelam/ plain metal along with split fabric magnetic/fabric tackable/white board/prelam/ plain metal. INTERMEDIATE BLOCKS on main spine Intermediate blocks are given in fabric/DL + Fabric/DL finsh. Wire Management through main spine- Wires shall be taken into the system through cable ducts from the junction boxes and it is carried upto the panels through concealed conduits inside the blocks. Side panels or legs - out of 25 mm thk prelam particle board with flat pvc lipping edge banding considered only on the open end conditions or metal powder coated legs at the end and shared condition. System shall also have 120 mm high powder coated standalone panel legs to give the system an elevated look. Worksurface - out of 25 mm thk prelam particle board with flat pvc lipping edge banding of size as per mentioned sizes. | 46 | Nos. |  | 0
| 3 Dr Metal pedestal: FREE STANDING PEDESTAL WITH FLAT METAL FRONT OF SIZE 390W X 435D X 646HT, 3DR = 2 BOX + 1 FILE, CENTRAL LOCKING. 0.8Mm thick CRCA for Body , Shell and Side Stiffners & bottom. 1.2 Mm thick for top and bottom stiffner. Metal front straight Edge. Swiveling non lockable castors mounted below the body shell. Epoxy polyester powder coated to the thickness of 50 microns. Key Board Pull Out Tray ( Metal KBPT): Size – 522 mm W x 405mm - 635mm D X 77mm – 105mm H, Metal Tray - Tray is made of 0.9 mm thick MS Sheet CRCA. (Size: 482(W) x 270(D) x 18(H) MM). CPU trolley - CPU Trolley Width - 230 - 345mm Depth - 226.0mm Height - 180mm Metal Tray - Tray is made of 1.0 mm thick MS CRCA Sheet and Side support is made of 0.8 mm thick MS CRCA Sheet. Castor - Lockable/Non-lockable twin wheel castors are injection molded in Black Nylon. etc. complet as directed and approved by Architect or Engineer In Charge |  |  |  | 0
5 | CABIN TABLE : 1500W X 600D MAIN DESK ,Providing and placing DESK based modular workstation with System ht - 1200 mm SCREENS: Main Fabric screen on stud. UNDERSTRUCTURE: Comprising of metal cross member between legs, DFINE PLUS legs made up of metal finish on end and shared leg with wire tray raiser the entire assemply is fixed to the worktop. Wire Management : Shared leg with wire tray raiser is given to pull wires from the floor junction box upto the power box fixed under neath the worktop. Aluminium access flaps on worktop above power box cut out for accessing switches. To carry wires forward through w/s wire tray assembly is provided below worktops. MODESTY PANEL: Porforated metal modesty 0.8 mm thk.modesty is mounted under neath the worktop with the help of the brackets. Worksurface - out of 25 mm thk prelam particle board with flat pvc lipping edge banding of size 1200 mm w X 600 mm d. 3 Dr Metal pedestal: FREE STANDING PEDESTAL WITH FLAT METAL FRONT OF SIZE 390W X 435D X 646HT, 3DR = 2 BOX + 1 FILE, CENTRAL LOCKING. 0.8Mm thick CRCA for Body , Shell and Side Stiffners & bottom. 1.2 Mm thick for top and bottom stiffner. Metal front straight Edge. Swiveling non lockable castors mounted below the body shell. Epoxy polyester powder coated to the thickness of 50 microns. Key Board Pull Out Tray ( Metal KBPT): Size – 522 mm W x 405mm - 635mm D X 77mm – 105mm H, Metal Tray - Tray is made of 0.9 mm thick MS Sheet CRCA. (Size: 482(W) x 270(D) x 18(H) MM). CPU trolley - CPU Trolley , Width - 230 - 345mm , Depth - 226.0mm Height - 180mm, Metal Tray - Tray is made of 1.0 mm thick MS CRCA Sheet and Side support is made of 0.8 mm thick MS CRCA Sheet, Castor - Lockable/Non-lockable twin wheel castors are injection molded in Black Nylon. etc. complet as directed and approved by Architect or Engineer In Charge | 23 | Nos. |  | 0
6 | Providing & Fixing 1200w x 600d DESK based modular workstation with System ht - 1200 mm SCREENS: Main Fabric screen on stud. UNDERSTRUCTURE: Comprising of metal cross member between legs, DFINE PLUS legs made up of metal finish on end and shared leg with wire tray raiser the entire assemply is fixed to the worktop. Wire Management : Shared leg with wire tray raiser is given to pull wires from the floor junction box upto the power box fixed under neath the worktop. Aluminium access flaps on worktop above power box cut out for accessing switches. To carry wires forward through w/s wire tray assembly is provided below worktops. MODESTY PANEL: Porforated metal modesty 0.8 mm thk.modesty is mounted under neath the worktop with the help of the brackets. Worksurface - out of 25 mm thk prelam particle board with flat pvc lipping edge banding of size 1200 mm w X 600 mm d , 3 Dr Metal pedestal: FREE STANDING PEDESTAL WITH FLAT METAL FRONT OF SIZE 390W X 435D X 646HT, 3DR = 2 BOX + 1 FILE, CENTRAL LOCKING. 0.8Mm thick CRCA for Body , Shell and Side Stiffners & bottom. 1.2 Mm thick for top and bottom stiffner. Metal front straight Edge. Swiveling non lockable castors mounted below the body shell. Epoxy polyester powder coated to the thickness of 50 microns. Key Board Pull Out Tray ( Metal KBPT): Size – 522 mm W x 405mm - 635mm D X 77mm – 105mm H, Metal Tray - Tray is made of 0.9 mm thick MS Sheet CRCA. (Size: 482(W) x 270(D) x 18(H) MM). CPU trolley - CPU Trolley , Width - 230 - 345mm , Depth - 226.0mm Height - 180mm, Metal Tray - Tray is made of 1.0 mm thick MS CRCA Sheet and Side support is made of 0.8 mm thick MS CRCA Sheet, Castor - Lockable/Non-lockable twin wheel castors are injection molded in Black Nylon. etc. complet as directed and approved by Architect or Engineer In Charge | 0 | Nos. |  | 0
7 | roviding & Fixing 1350w x 600d DESK based modular workstation with System ht - 1200 mm SCREENS: Main Fabric screen on stud. UNDERSTRUCTURE: Comprising of metal cross member between legs, DFINE PLUS legs made up of metal finish on end and shared leg with wire tray raiser the entire assemply is fixed to the worktop. Wire Management : Shared leg with wire tray raiser is given to pull wires from the floor junction box upto the power box fixed under neath the worktop. Aluminium access flaps on worktop above power box cut out for accessing switches. To carry wires forward through w/s wire tray assembly is provided below worktops. MODESTY PANEL: Porforated metal modesty 0.8 mm thk.modesty is mounted under neath the worktop with the help of the brackets. Worksurface - out of 25 mm thk prelam particle board with flat pvc lipping edge banding of size 1200 mm w X 600 mm d , 3 Dr Metal pedestal: FREE STANDING PEDESTAL WITH FLAT METAL FRONT OF SIZE 390W X 435D X 646HT, 3DR = 2 BOX + 1 FILE, CENTRAL LOCKING. 0.8Mm thick CRCA for Body , Shell and Side Stiffners & bottom. 1.2 Mm thick for top and bottom stiffner. Metal front straight Edge. Swiveling non lockable castors mounted below the body shell. Epoxy polyester powder coated to the thickness of 50 microns. Key Board Pull Out Tray ( Metal KBPT): Size – 522 mm W x 405mm - 635mm D X 77mm – 105mm H, Metal Tray - Tray is made of 0.9 mm thick MS Sheet CRCA. (Size: 482(W) x 270(D) x 18(H) MM). CPU trolley - CPU Trolley , Width - 230 - 345mm , Depth - 226.0mm Height - 180mm, Metal Tray - Tray is made of 1.0 mm thick MS CRCA Sheet and Side support is made of 0.8 mm thick MS CRCA Sheet, Castor - Lockable/Non-lockable twin wheel castors are injection molded in Black Nylon. etc. complet as directed and approved by Architect or Engineer In Charge | 0 | Nos. |  | 0
8 | Providing & Fixing 1500w x 750d Canteen Table: Providing, supplying and placing of Table top should be made of 25min thk. MDF OSR board (Bottom side in white color) as per IS:12406 with membrane finish on top side. Legs should be made by welding the combination of MS ERW round Tube 063.5 x 2mm THK as per IS: 7138, flanges made CRCA sheet of 1.6mm thk. and 1.2mm thk. as per IS 513 and inside plates made of HR 5mm thk. sheet as per IS:2062. The Assembly will be epoxy polyester powder coated of minimum thickness 45 microns. The Table top will fold upside at offset center pivot provided on support bracket which should be Aluminum alloy (ADC12) pressure die cast part coated with epoxy polyester powder coating of minimum thickness of 45 microns. Table top connected with spring loaded mechanism with pull handle made of MS ERW 016x1 2mm thk with an insert tube of 012.7x1.6mm thk tube as per IS:7138 coated with epoxy polyester powder coated of minimum 45 micron thickness to operate table top. Legs should be provided with casters of 065mm lockable type for ease of movement and can be locked when required at any position etc. complet as directed and approved by Architect or Engineer In Charge | 7 | Nos. |  | 0
9 | Openable Storage: Providing and fixing Openable Storage of 750 x 450 x 740Ht:- Providing, supplying and placing of storage Body : Body is made from 18mm PLB with all the edges sealed with 0.8 mm thick PVC Edgeband. The Back panel is 9mm White PLT. The entire construction is ready to assemble unit and is assembled with suitable KD fittings. The shelves and separator panels ( if available ) is made from 18 mm white PLT and edges are sealed with 0.8 mm edge band. The bottom shelf is fixed and other shelves have one step adjustment for optimizing the space. Doors : Door Panels ae made from 18 mm PLB with 2 mm Edge band on all edges ad a flush Plastic handle is fitted vertically at the center of the door. The hinge door has suitable hinges and HDU is fitted with an adjustable fitting for height adjustment. HDU has a three point lock. All the storages are fitted with a 6 mm leveler at bottom for leveling etc. complet as directed and approved by Architect or Engineer In Charge | 0 | Nos. |  | 0
10 | Medium Height Storage W 750 X H 1190 X D 450: roviding, supplying and placing of storage Body : Body is made from 18mm PLB with all the edges sealed with 0.8 mm thick PVC Edgeband. The Back panel is 9mm White PLT. The entire construction is ready to assemble unit and is assembled with suitable KD fittings. The shelves and separator panels ( if available ) is made from 18 mm white PLT and edges are sealed with 0.8 mm edge band. The bottom shelf is fixed and other shelves have one step adjustment for optimizing the space. Doors : Door Panels ae made from 18 mm PLB with 2 mm Edge band on all edges ad a flush Plastic handle is fitted vertically at the center of the door. The hinge door has suitable hinges and HDU is fitted with an adjustable fitting for height adjustment. HDU has a three point lock. All the storages are fitted with a 6 mm leveler at bottom for leveling etc. complet as directed and approved by Architect or Engineer In Charge | 46 | Nos. |  | 0
11 | Low Height Openable Storage W 900 X H 740 X D 450: roviding, supplying and placing of storage Body : Body is made from 18mm PLB with all the edges sealed with 0.8 mm thick PVC Edgeband. The Back panel is 9mm White PLT. The entire construction is ready to assemble unit and is assembled with suitable KD fittings. The shelves and separator panels ( if available ) is made from 18 mm white PLT and edges are sealed with 0.8 mm edge band. The bottom shelf is fixed and other shelves have one step adjustment for optimizing the space. Doors : Door Panels ae made from 18 mm PLB with 2 mm Edge band on all edges ad a flush Plastic handle is fitted vertically at the center of the door. The hinge door has suitable hinges and HDU is fitted with an adjustable fitting for height adjustment. HDU has a three point lock. All the storages are fitted with a 6 mm leveler at bottom for leveling etc. complet as directed and approved by Architect or Engineer In Charge | 36 | Nos. |  | 0
12 | Medium Height Storage W 900 X H 1190 X D 450: Providing, supplying and placing of storage Body : Body is made from 18mm PLB with all the edges sealed with 0.8 mm thick PVC Edgeband. The Back panel is 9mm White PLT. The entire construction is ready to assemble unit and is assembled with suitable KD fittings. The shelves and separator panels ( if available ) is made from 18 mm white PLT and edges are sealed with 0.8 mm edge band. The bottom shelf is fixed and other shelves have one step adjustment for optimizing the space. Doors : Door Panels ae made from 18 mm PLB with 2 mm Edge band on all edges ad a flush Plastic handle is fitted vertically at the center of the door. The hinge door has suitable hinges and HDU is fitted with an adjustable fitting for height adjustment. HDU has a three point lock. All the storages are fitted with a 6 mm leveler at bottom for leveling etc. complet as directed and approved by Architect or Engineer In Charge. | 67 | Nos. |  | 0
19 | Double Faced Mobile Unit for Compactor : Providing, supplying and placing of storage Overall Dimensions of TD4 Solid back panel Single Static Drive Cover Unit 4 Bay(U/C + Fittings + Cover) shall be 4800mm (W) x400mm(D) x2502.5mm(H). The Construction shall be rigid knock down made out of 0.8 thick CRCA steel conforming to IS : 513 . Each body shall have a main unit plus add on units (1,2,3,4) . Finish shall be Epoxy polyester powder coated thickness of 40 microns . Shelf construction shall be made from CRCA steel 0.8 mm thick IS :513 . Uniformly distributed load capacity of 100Kg . Undercarriage shall have construction in welded frame made of HR sheet 3 mm thick conforming to IS:2062.The Movements shall be Drive Type configuration : In case of D4 movement of units is achieved mechanically through a Drive Wheel and Sprocket -Chain- Tensioner arrangement mounted rigidly onto body size .For D4 each movable undercarriage shall be provided with 4 rollers on the shaft for driving ,4 antifriction ball bearing for rolling and LD has 2 anti-tilt bearing assembly.The roller assembly comprises of a die-cast step wheel, 2 deep-groove ball bearings and a MS shaft. The step wheel is made of cast steel and is fitted onto the MS shaft using a feather key. The two ball bearings are then fastened on either side of the step wheel using circlips. This entire roller assembly is then snap-fitted into a wheel housing. The wheel housing is fixed in the U channel of the understructure using machine screws. This wheel-housing is made of engineering plastic material made by injection-molding process. The entire roller assembly is designed to withstand the maximum loads of the body.Fittings shall be centralized locking arrangement through locking stiffener mounted onto back of single last unit so that it gets locked on channels when all the units are brought together. When the last unit is twin movable , hinged doors are provided for the end bodies, so in this case locking stiffener is mounted onto drive unit cover. | 15 | Nos. |  | 0
| Each Drive Type units shall have Locking Knob near the drive wheel for manual locking of individual units when a person is using those units. Knob shall be rotated to unlock position when units are to be moved. End stoppers shall be provided to prevent derailment . Door locking shall be having hinged doors of recessed die cast handle cum lock giving 3 way locking through a lever & shooting bolts. Also total no. of loading levels per understructure shall be 24 for SD4. The nuts & bolts are galvanized / blackodized / Zn Plated. Also total no. of loading levels per understructure shall be 30 for TD3. Label holder - It is an aluminium extrusion of length 396mm for LD/SD and 796mm for TD, fitted on to front cover of body. The Paper is 300GSM matt milky white sticker paper, to be inserted into the aluminium extrusion. The length of paper is 394mm for LD/SD and 794mm for TD. Over that a transparent plastic of corresponding length of 150-300 micron polythene is to be inserted.TD units are designed with tie rod assembly options as well. it acts as a substitute to the back panels (only in twin body) if the customer chooses to not have back panels. The assembly consists of 2 tie rods, 4 fixing brackets and 2 turnbuckles. The tie rods are fixed in a shape of ‘X’ between two opposite shelves. The tie rods are made of 4mm diameter rods of MS while the fixing brackets are made of 2mm thk. CRCA Steel conforming to IS: 513 Gr.D. This assembly is available for both heights – 1980H and 2361H. |  |  |  | 0
| FURNITURE WORK OF SOFA, CHAIR , WARDROBE AND MODULAR KITCHEN |  |  |  | 0
1 | Providing, supplying and placing of High Back Chair SEAT/BACK ASSEMBLY with Neck Rest : The Cushioned seat assembly consshould be ts of seat outer (material-30% Glass Fiber Nylon)& upholstered Seat inner (material- Poly Propylene) with moulded Polyurethane foam & polyster fabric. The Net Back should be made up of Back outer (material-Glass Fiber Filled Nylon)& Back inner (material- PP) and upholstered using Polyester Mesh fabric with high tenacity yarn. Full Back Size: 46.5 cm. (W) x 60.0 cm. (H) Seat Size : 51.0 cm. (W) x 49.0 cm. (D) HIGH RESILIENCE (HR) POLYURETHANE FOAM: The HR Polyurethane foam should be moulded with density = 45 +/- 2 kg/m³ and Hardness load 12 +/- 2 kgf for 25% compression. BACK SPINE: The support spine should be made up of High Pressure Die cast polished hed Aluminum. ARMRESTS : The armrest should be having two adjustment, Height (6.0±0.5cm) and Depth (6.0±0.5cm). Height adjustment should be provided in Aluminum structure of armrest which should be connected to Aluminum Back spine and should be operated by button. The depth adjustment should be provided in pad which should be fixed to armrest structure. Armrest Top should be made up of PU molded over plastic inner. ACTIVE BIO-SYNCHRO mechanism: The adjustable tilting mechanism should be designed with the following features: • 360° revolving type • Front-pivot for tilt with feet resting on ground & continuous lumber support ensuring more comfort • Tilt tension adjustment can be operated in seating position • 5 position Tilt limiter giving option of variable tilt angle to the chair • Seat / back tilting ratio of 1:2 • The mechanism housing should be made up of HPDC Aluminum & black powder coated (DFT 40 to 60 micron) SEAT DEPTH ADJUSTMENT: Seat depth adjustment should be integrated in the seat through a sliding mechanism. Seat depth adjustment range should be of 3.75±0.1 cm LUMBAR SUPPORT ASSEMBLY: The Lumbar support assembly should consist of lumbar spine (material-Glass Fiber Filled Nylon) which should be fixed to Aluminum Back spine. The Lumbar pad | 6 | Nos. |  | 0
2 | Providing, supplying and placing of High Back Chair SEAT/BACK ASSEMBLY with full bac : The Cushioned seat assembly consshould be ts of seat outer (material-30% Glass Fiber Nylon)& upholstered Seat inner (material- Poly Propylene) with moulded Polyurethane foam & polyster fabric. The Net Back should be made up of Back outer (material-Glass Fiber Filled Nylon)& Back inner (material- PP) and upholstered using Polyester Mesh fabric with high tenacity yarn. Full Back Size: 46.5 cm. (W) x 60.0 cm. (H) Seat Size : 51.0 cm. (W) x 49.0 cm. (D) HIGH RESILIENCE (HR) POLYURETHANE FOAM: The HR Polyurethane foam should be moulded with density = 45 +/- 2 kg/m³ and Hardness load 12 +/- 2 kgf for 25% compression. BACK SPINE: The support spine should be made up of High Pressure Die cast polished hed Aluminum. ARMRESTS : The armrest should be having two adjustment, Height (6.0±0.5cm) and Depth (6.0±0.5cm). Height adjustment should be provided in Aluminum structure of armrest which should be connected to Aluminum Back spine and should be operated by button. The depth adjustment should be provided in pad which should be fixed to armrest structure. Armrest Top should be made up of PU molded over plastic inner. ACTIVE BIO-SYNCHRO mechanism: The adjustable tilting mechanism should be designed with the following features: • 360° revolving type • Front-pivot for tilt with feet resting on ground & continuous lumber support ensuring more comfort • Tilt tension adjustment can be operated in seating position • 5 position Tilt limiter giving option of variable tilt angle to the chair • Seat / back tilting ratio of 1:2 • The mechanism housing should be made up of HPDC Aluminum & black powder coated (DFT 40 to 60 micron) SEAT DEPTH ADJUSTMENT: Seat depth adjustment should be integrated in the seat through a sliding mechanism. Seat depth adjustment range should be of 3.75±0.1 cm LUMBAR SUPPORT ASSEMBLY: The Lumbar support assembly should consist of lumbar spine (material-Glass Fiber Filled Nylon) which should be fixed to Aluminum Back spine. The Lumbar pad | 27 | Nos. |  | 0
3 | Providing & Supplying Chair with Nect Rest:- Providing, supplying and placing of High Back Chair SEAT/BACK A SSEMBLY: The seat is made up of 1.2 + 0.1cm thk. hot pressed plywood measured .The Back is made up of injection mou1ded glass filled nylon & upholstered using Mesh fabric with high tenacity yarn. * SEAT SIZE(Larger Seat Depth) : 47.0 cm. (W) x 51.5 cm (D) * BACK SIZE : 45.0 cm. (\/V) x 65.3 cm. (H) HIGH RESILIENCE (HR) POLYURETHANE FOAM: The HR polyurethane seat foam is moulded with density 45+/-2 kg/m° and hardness 16 + 2 kgf as per IS:7888 for 25% compression. ARMRESTS : The adjustable armrest is designed with the following features : • Up-Down adjustment— 8 steps (8 0+0.Scm range) • Height adjustable armrest structure which is Powder Coated & fitted with an armrest top. • Fixed Armrest Top is PU moulded over metal insert. LUMBAR SUPPORT ASSEMBLY: The Lumbar support consists of polypropylene pad with moulded polyurethane foam & covered with polyester fabric.The Height of Lumbar pad can be adjusted through two projecting knobs provided on the rear side of the pa6. Lumbar pad has an adjustment of 8.0 + 0.5 cm in height. FRONT PIVOT SYNCHRO MECHANISM: The adjustable tilting mechanism is designed with the following features. • 360° revolving type. • Single point control. • Front-pivot for tilt with feet resting on ground ensuring more comfort. » Tilt tension adjustment. • 4-position locking with anti-shock feature. • Seat/back tilting ratio of 1:2. PNEUMATIC HEiGHT ADJUSTMENT. The pneumatic height adjustment has an adjustment stroke oi 10.0 + 0.3 cn°. Pedestal Assembly : the pedestal is injection moulded in black 30% glass filled nylon and fitted with 5 nos. twin wheel castors. H=The pedestal pitch center dia is 66.1+0.5 cm | 24 | Nos. |  | 0
4 | Providing, supplying and placing of High Back Chair SEAT/BACK A SSEMBLY: The seat is made up of 1.2 + 0.1cm thk. hot pressed plywood measured .The Back is made up of injection mou1ded glass filled nylon & upholstered using Mesh fabric with high tenacity yarn. * SEAT SIZE(Larger Seat Depth) : 47.0 cm. (W) x 51.5 cm (D) * BACK SIZE : 45.0 cm. (\/V) x 65.3 cm. (H) HIGH RESILIENCE (HR) POLYURETHANE FOAM: The HR polyurethane seat foam is moulded with density 45+/-2 kg/m° and hardness 16 + 2 kgf as per IS:7888 for 25% compression. ARMRESTS : The adjustable armrest is designed with the following features : • Up-Down adjustment— 8 steps (8 0+0.Scm range) • Height adjustable armrest structure which is Powder Coated & fitted with an armrest top. • Fixed Armrest Top is PU moulded over metal insert. LUMBAR SUPPORT ASSEMBLY: The Lumbar support consists of polypropylene pad with moulded polyurethane foam & covered with polyester fabric.The Height of Lumbar pad can be adjusted through two projecting knobs provided on the rear side of the pa6. Lumbar pad has an adjustment of 8.0 + 0.5 cm in height. FRONT PIVOT SYNCHRO MECHANISM: The adjustable tilting mechanism is designed with the following features. • 360° revolving type. • Single point control. • Front-pivot for tilt with feet resting on ground ensuring more comfort. » Tilt tension adjustment. • 4-position locking with anti-shock feature. • Seat/back tilting ratio of 1:2. PNEUMATIC HEiGHT ADJUSTMENT. The pneumatic height adjustment has an adjustment stroke oi 10.0 + 0.3 cn°. Pedestal Assembly : the pedestal is injection moulded in black 30% glass filled nylon and fitted with 5 nos. twin wheel castors. H=The pedestal pitch center dia is 66.1+0.5 cm TWIN WHEEL CASTORS: The twin wheel castors are injection moulded in black Nylon. | 126 | Nos. |  | 0
5 | Providing & Arrangemnt of High Back Chair - Providing, supplying and placing of High Back Chair / AND MID BACK SEAT/BACK ASSEMBLY : The Cushioned seat should be made of Injection molded Plastic outer & inner. Plastic Inner should be upholstered with pure leather and moulded High Resilience (HR) Polyurethane foam of Density 45±2 kg/m3,and hardness load 16 ± 2 kgf for 25% compression.The Cushioned back should be made of PU Foam with insitu molded MS E.R.W Round Tube of size 1.9±0.03cm x 0.16 ±0.0128cm. It upholstered with Pure Leather. Seat SIZE : 47.6 cm. (W) x 49.2 cm. (D) BACK SIZE : 47.5 cm. (W) x 77 cm. (D) ARMRESTS: The armrest top should be moulded from polyurethane(PU), upholstered in pure leather and mounted on to a drop lift adjustable type tubular armrest support made of 03.81±0.03 cm x 0.2±0.01 cm thk M.S E.R.W tube having chrome plated finish.The armrest height adjustable up to 6.5±0.5cm in 5 steps. ACTIVE BIO-SYNCHRO mechanism: The adjustable tilting mechanism should be designed with the following features: • 360° revolving type. • Front-pivot for tilt with feet resting on ground and continuous lumbar support ensuring more comfort. • Tilt tension adjustment can be operated in seating position. • 5-position Tilt limiter giving option of variable tilt angle to the chair. • Seat/back tilting ratio of 1: 2 • The mechanism housing should be made up of HPDC Aluminium black powder coated. SEAT DEPTH ADJUSTMENT: Seat depth adjustment should be integrated in the seat through a sliding mechanism. Seat depth adjustment range should be of 6.0±0.5 cm. ADJUSTABLE BACK SUPPORT: Back Frame should be connected to the Up/Dn mechanism housed in Plastic T spine. It can be adjusted in the range of 7.42±0.5 cm for the comfortable back support to suit individual need. PNEUMATIC HT. ADJUSTMENT: The pneumatic height adjustment has an adjustment stroke of 10.0±0.3 cm. PEDESTAL ASSEMBLY The pedestal should be High Pressure Die cast polished Aluminium and fitted | 5 | Nos. |  | 0
6 | Providing & Arrangemnt of Mid Back Chair - Providing, supplying and placing of High Back Chair / AND MID BACK SEAT/BACK ASSEMBLY : The Cushioned seat should be made of Injection molded Plastic outer & inner. Plastic Inner should be upholstered with pure leather and moulded High Resilience (HR) Polyurethane foam of Density 45±2 kg/m3,and hardness load 16 ± 2 kgf for 25% compression.The Cushioned back should be made of PU Foam with insitu molded MS E.R.W Round Tube of size 1.9±0.03cm x 0.16 ±0.0128cm. It upholstered with Pure Leather. Seat SIZE : 47.6 cm. (W) x 49.2 cm. (D) BACK SIZE : 47.5 cm. (W) x 77 cm. (D) ARMRESTS: The armrest top should be moulded from polyurethane(PU), upholstered in pure leather and mounted on to a drop lift adjustable type tubular armrest support made of 03.81±0.03 cm x 0.2±0.01 cm thk M.S E.R.W tube having chrome plated finish.The armrest height adjustable up to 6.5±0.5cm in 5 steps. ACTIVE BIO-SYNCHRO mechanism: The adjustable tilting mechanism should be designed with the following features: • 360° revolving type. • Front-pivot for tilt with feet resting on ground and continuous lumbar support ensuring more comfort. • Tilt tension adjustment can be operated in seating position. • 5-position Tilt limiter giving option of variable tilt angle to the chair. • Seat/back tilting ratio of 1: 2 • The mechanism housing should be made up of HPDC Aluminium black powder coated. SEAT DEPTH ADJUSTMENT: Seat depth adjustment should be integrated in the seat through a sliding mechanism. Seat depth adjustment range should be of 6.0±0.5 cm. ADJUSTABLE BACK SUPPORT: Back Frame should be connected to the Up/Dn mechanism housed in Plastic T spine. It can be adjusted in the range of 7.42±0.5 cm for the comfortable back support to suit individual need. PNEUMATIC HT. ADJUSTMENT: The pneumatic height adjustment has an adjustment stroke of 10.0±0.3 cm. PEDESTAL ASSEMBLY The pedestal should be High Pressure Die cast polished Aluminium and fitted | 52 | Nos. |  | 0
7 | Providing & Arrangemnt of ADJUSTABLE NECK RESTChairs: Providing, supplying and placing of MID Back Chair SEAT/BACK ASSEMBLY: The seat is made up of 1.5 ± 0.1cm thk. hot pressed plywood measured SEAT SIZE(Larger Seat Depth) {PULSAL}: 47.0 cm. (W) x 51.5 cm. (D) BACK SIZE (PULSAX,PULSAL):45.0 cm. (W) x 65.3 cm. (H) HIGH RESILIENCE (HR) POLYURETHANE FOAM: The HR polyurethane foam is moulded with density =55+/-2 kg/m3 and hardness 16 ± 2 kgf as per IS:7888 for 25% compression. ARMRESTS (ADJUSTABLE){PULSAX, PULSAL}: The adjustable armrest is designed with the following features: • Up-Down adjustment- 6 steps (7.2 ± 0.5cm range) • Armrest top is mounted on Armrest structure made of glass filled Nylon. • Armrest Top is PU moulded over glass filled Nylon insert. LUMBAR SUPPORT ASSEMBLY: The Lumbar support consists of polypropylene pad.The Height of Lumbar pad can be adjusted through two projecting knobs provided on the rear side of the pad. Lumbar pad has an adjustment of 8.0 ± 0.5 cm in height. FRONT PIVOT SYNCHRO MECHANISM: The adjustable tilting mechanism is designed with the following features. • 360° revolving type. • Single point control. • Front-pivot for tilt with feet resting on ground ensuring more comfort. • Tilt tension adjustment. • 4-position locking with anti-shock feature. • Seat/back tilting ratio of 1:2. PNEUMATIC HEIGHT ADJUSTMENT: The pneumatic height adjustment has an adjustment stroke of 10.0 ± 0.3 cm. PEDESTAL ASSEMBLY: The pedestal is injection moulded in black 30% glass-filled Nylon and fitted with 5 nos. twin wheel castors. The pedestal pitch-center dia is 066.1 ± 0.5 cm. (76.1 ± 1.0 cm. with castors). | 121 | Nos. |  | 0
8 | Providing & Supplying 3 seater Sofa of approved make :- • Providing & fixing 3 Seater Sofa Width (W): 206.0 CM. Depth (D): 90.5 CM. Height (H): 85.5 CM. Seat Height (SH): 45.0 CM. Providing, supplying and placing of sofa 1)SEAT FOAM : The seat is made up of PU foam in Density 28 ±2 kg/cu.mtr with an additional top layer of supersoft PU foam in Density 32 ± 2 kg/cu, upholstered with fabric or leatherette. 2)BACK FOAM : The back is made up of PU foam in Density 28 ± 2 kg/cu. mtr with two additional top layer of supersoft foam of density 32±2 kg/cu. mtr, upholstered with fabric or leatherette. 3)UNDERSTRUCTRE : Understructure is made up of 1.2±0.1 cm. thick hot pressed plywood [moisture resistance & termite proof as per IS:303] & pinewood of cross sections devoid of major knots & surface defects. 6 nos. per seat & 3.8mm Dia zigzag spring assembly is mounted over understructure for cushioning purpose. 4)LEG ASSEMBLY : It is a welded Assembly made in Stainless steel (grade SS 202) tube & plate with plastic endcap. etc. complete | 7 | Nos. |  | 0
9 | Providing & Supplying 2 seater Sofa of approved make :- Providing & fixing 2Seater Sofa Width (W): 146.0 CM. Depth (D): 90.5 CM. Height (H): 85.5 CM. Seat Height (SH): 45.0 CM Providing, supplying and placing of sofa 1)SEAT FOAM : The seat is made up of PU foam in Density 28 ±2 kg/cu.mtr with an additional top layer of supersoft PU foam in Density 32 ± 2 kg/cu, upholstered with fabric or leatherette. 2)BACK FOAM : The back is made up of PU foam in Density 28 ± 2 kg/cu. mtr with two additional top layer of supersoft foam of density 32±2 kg/cu. mtr, upholstered with fabric or leatherette. 3)UNDERSTRUCTRE : Understructure is made up of 1.2±0.1 cm. thick hot pressed plywood [moisture resistance & termite proof as per IS:303] & pinewood of cross sections devoid of major knots & surface defects. 6 nos. per seat & 3.8mm Dia zigzag spring assembly is mounted over understructure for cushioning purpose. 4)LEG ASSEMBLY : It is a welded Assembly made in Stainless steel (grade SS 202) tube & plate with plastic endcap. etc. complete | 2 | Nos. |  | 0
10 | Providing & Supplying Sofa Chair of approved make :- Providing & fixing1 seater Width (W): 86.0 CM. Depth (D): 90.5 CM. Height (H): 85.5 CM. Seat Height (SH): 45.0 CM. Providing, supplying and placing of sofa 1)SEAT FOAM : The seat is made up of PU foam in Density 28 ±2 kg/cu.mtr with an additional top layer of supersoft PU foam in Density 32 ± 2 kg/cu, upholstered with fabric or leatherette. 2)BACK FOAM : The back is made up of PU foam in Density 28 ± 2 kg/cu. mtr with two additional top layer of supersoft foam of density 32±2 kg/cu. mtr, upholstered with fabric or leatherette. 3)UNDERSTRUCTRE : Understructure is made up of 1.2±0.1 cm. thick hot pressed plywood [moisture resistance & termite proof as per IS:303] & pinewood of cross sections devoid of major knots & surface defects. 6 nos. per seat & 3.8mm Dia zigzag spring assembly is mounted over understructure for cushioning purpose. 4)LEG ASSEMBLY : It is a welded Assembly made in Stainless steel (grade SS 202) tube & plate with plastic endcap. etc. complete | 4 | Nos. |  | 0
11 | Providing & Fixing center table: Providing, supplying and placing of Center table. Width of table= 112.0 cm, Depth=60.0 cm, height=34.9 cm. table glass: It is 10 ±0.3 mm thick black tinted Toughened glass UV glued with bushes made in SS 202 grade for focing with understructure. PISA CENTER TABLE UNDERSTRUCTURE: It is a welded Assembly made in SS202 grade Dia. 12±0.04 as per IS:1762." etc. complete. | 2 | Nos. |  | 0
12 | Providing & Fixing pisa corner table: 1)Providing, supplying and placing of corner table Width of table= 112.0 cm, Depth=60.0 cm, height=34.9 cm. TABLE GLASS: It is 10 ±0.3 mm thick black tinted Toughened glass UV glued with bushes made in SS 202 grade for focing with understructure. 2)PISA SIDE UNDERSTRUCTURE: It is a welded Assembly made in SS202 gradeDia. 12±0.04 as per IS:1762. | 7 | Nos. |  | 0
13 | roviding, supplying and placing of cafe chair.The Seat and Back should be made up of injection moulded indoor grade PolyPropylene compound SEAT SIZE : 52.5 cm. (W) x 53.2 cm. (D) BACK SIZE : 51.6 cm. (W) x 40.5 cm. (H).The powder coated ( DFT 50±10 microns ) welded tubular frame should be made from 0 2.22 ± 0.03 cm x 0.12 ± 0.0128 cm and 3.5 ± 0.03 cm x 1.5 ± 0.03 cm x 0.12 ± 0.0128 cm stainless steel 202 grade tube. The shoes should be made of indoor grade PolyPropylene compound and snap fitted with tubular frame. | 30 | Nos. |  | 0
14 | Providing & Supplying Sofa Chair of approved make : Providing, supplying and placing of sofa 1 seater Overall Size :Width : 92cm Depth : 92cm Height : 89cm Seating Height : 47.5cm THREAD : Nylon . Material Handling Data Sheet (MSDS) for Glue Standard of Plywood used: IS 303 Commercial Plywood , Thickness 12mm Orlando 2 seater Overall Size :Width : 137cm Depth : 92cm Height : 89cm Seating Height : 47.5cm THREAD : Nylon . Material Handling Data Sheet (MSDS) for Glue Standard of Plywood used: IS 303 Commercial Plywood , Thickness 12mm •Pure leather upholstery that stretches and moulds to the shape of the individual frame without sagging, losing form, cracking, or peeling. • Recron-filled high backrest that supports the entire body along with the shoulder and head for enhanced comfort. • Demarcated seats filled with soft foam with symmetrical stitching lines. • Elevated from the ground which facilitates cleaning. • Excellent craftsmanship with aesthetic piping and rounded soft edges. • Enhanced longevity owing to Double Webbing – S-spring + Nylon. • Solid wood frame along with the plywood cross section offers more rigidity to the sofa | 2 | Nos. |  | 0
15 | Providing & Supplying two seater of approved make Providing, supplying and placing of sofa 2 seater Overall Size :Width : 92cm Depth : 92cm Height : 89cm Seating Height : 47.5cm THREAD : Nylon . Material Handling Data Sheet (MSDS) for Glue Standard of Plywood used: IS 303 Commercial Plywood , Thickness 12mm Orlando 2 seater Overall Size :Width : 137cm Depth : 92cm Height : 89cm Seating Height : 47.5cm THREAD : Nylon . Material Handling Data Sheet (MSDS) for Glue Standard of Plywood used: IS 303 Commercial Plywood , Thickness 12mm •Pure leather upholstery that stretches and moulds to the shape of the individual frame without sagging, losing form, cracking, or peeling. • Recron-filled high backrest that supports the entire body along with the shoulder and head for enhanced comfort. • Demarcated seats filled with soft foam with symmetrical stitching lines. • Elevated from the ground which facilitates cleaning. • Excellent craftsmanship with aesthetic piping and rounded soft edges. • Enhanced longevity owing to Double Webbing – S-spring + Nylon. • Solid wood frame along with the plywood cross section offers more rigidity to the sofa | 2 | Nos. |  | 0
16 | Providing & Supplying PREMIUM LOUNGE 3 Seater Sofa: Providing, supplying and placing of sofa 3 Seater Overall size: Width :2930 mm, Depth :1000mm ,Height : 800mm, Seat Height :1000 mm 1 Seater Overall size: Width : 960 mm, Depth :1000mm ,Height : 800mm, Seat Height :460 mm Upholstery • Material : Half Leather Touch Point in pure leather and non touch point in Syn leather • Shade : Tan • Thickness : 1 mm Frame : • Material : Pine Wood • Moisture content : 10 - 12 % • Thickness of Plywood used : 12 mm & 18 mm Seat Foam : • Material : Slab stock • Density : 30D Hr soft + 28D Back Foam : • Material : Slab stock • Density : 23D SOFT + 23D SOFT + 30D HR Head Rest : •Material : Slab stock • Density : 23D soft + 23D Soft Webbing : • Material : S spring + cross membrane Legs : • Material : SS | 6 | Nos. |  | 0
17 | Wardrobe with Mirror @ 900LX 600DX 1965H for Residnetial Flats Providing and Fixing Wardrobe with Mirror of size 900LX 600DX 1965H The wardrobe side panels and doors are made up of 18mm thick Prelam Particle Board with both side decorative laminate. All exposed edges are sealed with 2mm thick PVC edge Banding. The shelves are made of 18mm thick Prelam Particle Board with decorative laminate on both sides. The top is made of 36mm prelam particle board with decorative laminate on both sides. (18mm Prelam Particle board and 18mm batons on all sides to achieve 36mm overall thickness). The exposed edges of the top are sealed with 2mm thick PVC edge Banding. The top most part of the wardrobe has an aluminum hanger rod of EBCO make. One drawer of size 400(W) x 150(H) x 450 (D) made of 18mm thick prelam Particle Board has been considered. The drawer will have a multipurpose lock of EBCO premium make. The wardrobe handles are Satin SS finish of 160mm pitch. The wardrobe has a multipurpose lock of EBCO make. All hinges considered are Hettich make. Necessary good quality hardwares have been considered as required. | 27 | Nos. |  | 0
18 | Modular Kitchen For Residential Flats Providing and Fixing Modular kitchenas per detailed drawings with complete set of trolly, fixtures and fastners etc. complete(The width and height of individual compartments shall be kept as directed by Engineer-in-charge) | 13 | Nos. |  | 0
19 | Providing, supplying and placing of sofa 1)SIDE FRAME ASSEMBLY: The side frame assembly should be fitted to the two ends of the connecting beam assembly to form the leg-cum-armrest assembly. It should be made of 0 3.81 ±0.03cm. x 0.2 ±0.016cm. thick cmx0.16cnn and black powder coated ( DFT 40-60 microns ). The ends should be fitted with ABS moulded end caps. 2)TIE MEMBER: It should be the connecting beam assy. which holds the two side frames to each other. 2 nos. tie members should be used to connect the side frames. The tie-member should be of 0 3.81 ±0.03cm. x 0.2 ±0.016cm. thick cm x 0.16cm and black powder coated ( DFT 40-60 microns ). The seat/back assemblies should be mounted on one of the tie-member which has 5.0 ±0.1cm x 5.0 ±0.1 cm x 0.5 ±0.1cm. thk -- 5.5 ±0.1cm Long MS. Std. angles welded to mount the seat and back. 3)SEATREST ASSEMBLY:The seat rest assembly consshould be ts of a fabricated inner-frame assembly insitu-moulded High Resilience (HR) Polyurethane foam having density = 45 +1- 2 Kg/m3 with Hardness load 25 ± 2 kgf for 25% compression of the foam. The complete moulded seat rest assembly should be covered with a replaceable fabric upholstery cover *SEAT SIZE: 52.0cm. (W) X 50.0cm. (D) X 6.0cm. (T) 4)BACKREST ASSEMBLY:The backrest assembly should be flexing type and consshould be ts of a fabricated inner-frame assembly insitu-moulded with High Resilience (HR) Polyurethane foam having density = 45 +1- 2 Kg/m3 with Hardness load 14 ± 2 kgf for 25% compression of the foam. The complete moulded backrest assembly should be covered with a replaceable fabric upholstery cover. *BACK SIZE: 52.0cm. (W) X 59.0cm. (H) X 6.0cm. (T) 5)ADJ. GLIDES: The adj. glide should be injection moulded in black Nylon & fitted to the front end of side frame assembly along with ABS moulded adj. Glide base to take cshould be or unleveled floor surface. | 8 | Nos. |  | 0
| FURNITURE TOTAL AMOUNT |  |  |  | 0