## New Template
*** Column A to D are fixed & Mandatory Columns. Do not delete columns.
GroupName | SubGroupName1 | SubGroupName2 | ItemName | SrNo | Description | UnitName | TenderQty | TenderRate | Remark
Earthing Work | Ground Earthing | Ground Earthing2 | Supply, installation, testing & commissioning of Maintenance Free earthing | 1 | Supply, installation, testing & commissioning of Maintenance Free earthing is made of 200µm (0,20mm) -copper-bonded steel earth road 6 Mtr length as per specification, drawing and as per the instruction of Engineer-in-charge. The unit rate shall include Excavation & backfilling (Make a pit preferably of 8-10 inch dia upto 6 meter length), resistance lowering grounding minerals to increase the overall conductive surface area inorder to ower the ohmic value and also to minimize the corrosion process, highly conductive Copper & Complete RCC chamber 450x450 inner size with RCC cover with handle , proper water pouring upto 6-7 days after installation. Contractor has to take earth resisteance testing reading and submit the earth testing report. Contractor has to mark earth pit number, resistance value and testing done & due date at each and every earthing on 450mm x 450 mm, 3mm thick plate with rode and grouted with concrete. 20mm dia, 6 meter length maintanance free earthing road with appro x 40Kg Resistance lowering compound Earthing. All Joint to Brazed where copper and weld where GI . Brass Nut bolt to be used in case of Copper connection at rod and GI nut bolt in case of GI | Nos | 6 | 20557 | R1
Earthing Work | Ground Earthing |  | Providing standard copper plate earth station | 2 | Providing standard copper plate earth station 6m at mtr depth ,with 600x600x 6 mm thick copper plate, 40mm dia, 5.5 mtr GI pipe with 25X6 copper strips runs on both(2 nos ) sides up to top of the earth pit including excavation and construction of brick pedestal providing meshed funnel, CI cover and other Civil works, spreading a homogeneous mixture of salt 40 Kg , charcoal (40 Kg) around the plate etc completely as per IS 3043, latest revision. Complete RCC chamber 450x450 inner size with RCC cover with handle , proper water pouring upto 6-7 days after installation. Contractor has to take earth resisteance testing reading and submit the earth testing report. Contractor has to mark earth pit number, resistance value and testing done & due date at each and every earthing on 450mm x 450 mm, 3mm thick plate with rode and grouted with concrete. | Nos | 6 | 48200 | R1
Earthing Work | Ground Earthing |  | Eart Strip | 3 | Earth Strip : Supply, installation, testing and commissioning of G.I./Copper earthing loop / grid conductors/Cu. Cables of following sizes along the cable trenchs / cable trays / on the wall or structures / buried in ground (300-500mm depth) including excavation and back filling. Installation shall include the welding at joints in case of GI and Brazed in case of Cu and providing anti corrosive point (black butimine) at the welded portion and clamping using G.I. clamps and necessary hardware and materials as per standard drawings, specifications and directions of Engineer-in-charge. Clamping on wall or on open surface to be done by installing insulator support.50 mm x 6 mm G.I.Earthing strip | Mtr | 100 | 559 | R1
Earth Stripping |  |  | GI Earth Strip | 4 | 50 mm x 6 mm G.I.Earthing strip | Mtr | 100 | 259 | R1
Earth Stripping |  |  | SWG Wire | 4 | 8 SWG G.I.wire | Mtr | 70 | 32 | R1
Earth Stripping |  |  | 50 mm x 6 mm Copper Earthing strip | 4 | 50 mm x 6 mm Copper Earthing strip | Mtr | 100 | 2860 | R1
Earth Stripping |  |  | 25 mm x 6 mm Copper Earthing strip | 4 | 25 mm x 6 mm Copper Earthing strip | Mtr | 20 | 1440 | R1
Earth Stripping |  |  | EARTHING WIRE | 4 | Providing, laying, testing and commissioning of following 1100 volts grade PVC insulated sheathed copper conductor unarmored cable of approved make including termination on both end with copper thimbles, fixing hardware complete as required. Single core 50 sq.mm Green colour cable | Mtr | 50 | 75 | R1
Earth Stripping |  |  | Providing, laying, testing and commissioning | 4 | Providing and fixing in position the following size 2 mm thick heavy duity fire rated PVC conduit concealed or exposed including digging, cutting, filling of chase all accessories i.e. bends, junction boxes, with cover plates of approved make and design. 25 mm | Mtr | 25 | 45 | R1
CONDUIT |  |  | CONDUIT Piping | 5 | Providing and fixing of Conduit piping of 6 mm | Mtr | 100 | 101 | R1

## old Template
BOQ Earthing required at Sub station (KCO)
Sr. No. | Item Name | Material Description | Unit | Qty | Composite Rate | Composite Amount
1 | Earthing Work | Supply, installation, testing & commissioning of Maintenance Free earthing is made of 200μm (0,20mm) -copper-bonded steel earth road 6 Mtr length as per specification, drawing and as per the instruction of Engineer-in-charge. The unit rate shall include Excavation & backfilling (Make a pit preferably of 8-10 inch dia upto 6 meter length), resistance lowering grounding minerals to increase the overall conductive surface area inorder to ower the ohmic value and also to minimize the corrosion process, highly conductive Copper & Complete RCC chamber 450x450 inner size with RCC cover with handle , proper water pouring upto 6-7 days after installation. Contractor has to take earth resisteance testing reading and submit the earth testing report. Contractor has to mark earth pit number, resistance value and testing done & due date at each and every earthing on 450mm x 450 mm, 3mm thick plate with rode and grouted with concrete. 20mm dia, 6 meter length maintanance free earthing road with appro x 40Kg Resistance lowering compound Earthing. All Joint to Brazed where copper and weld where GI . Brass Nut bolt to be used in case of Copper connection at rod and GI nut bolt in case of GI | Nos | 6 | 20557 | 123342
2 | Earthing Work | Providing standard copper plate earth station 6m at mtr depth ,with 600x600x 6 mm thick copper plate, 40mm dia, 5.5 mtr GI pipe with 25X6 copper strips runs on both(2 nos ) sides up to top of the earth pit including excavation and construction of brick pedestal providing meshed funnel, CI cover and other Civil works, spreading a homogeneous mixture of salt 40 Kg , charcoal (40 Kg) around the plate etc completely as per IS 3043, latest revision. Complete RCC chamber 450x450 inner size with RCC cover with handle , proper water pouring upto 6-7 days after installation. Contractor has to take earth resisteance testing reading and submit the earth testing report. Contractor has to mark earth pit number, resistance value and testing done & due date at each and every earthing on 450mm x 450 mm, 3mm thick plate with rode and grouted with concrete. | Nos | 6 | 48200 | 289200
3 | Earthing Work | Earth Strip : Supply, installation, testing and commissioning of G.I./Copper earthing loop / grid conductors/Cu. Cables of following sizes along the cable trenchs / cable trays / on the wall or structures / buried in ground (300-500mm depth) including excavation and back filling. Installation shall include the welding at joints in case of GI and Brazed in case of Cu and providing anti corrosive point (black butimine) at the welded portion and clamping using G.I. clamps and necessary hardware and materials as per standard drawings, specifications and directions of Engineer-in-charge. Clamping on wall or on open surface to be done by installing insulator support.
|  | 50 mm x 6 mm G.I.Earthing strip | Mtr | 100 | 259 | 25900
|  | 8 SWG G.I.wire | Mtr | 70 | 32 | 2240
|  | 50 mm x 6 mm Copper Earthing strip | Mtr | 100 | 2860 | 286000
|  | 25 mm x 6 mm Copper Earthing strip | Mtr | 20 | 1440 | 28800
4 | Earthing Work | EARTHING WIRE
Providing, laying, testing and commissioning of following 1100 volts grade PVC insulated sheathed copper conductor unarmored cable of approved make including termination on both end with copper thimbles, fixing hardware complete as required.
a) |  | Single core 50 sq.mm Green colour cable | Mtr | 0 | 0 | 0
5 | Earthing Work | CONDUIT
Providing and fixing in position the following size 2 mm thick heavy duity fire rated PVC conduit concealed or exposed including digging, cutting, filling of chase all accessories i.e. bends, junction boxes, with cover plates of approved make and design.
a) |  | 25 mm | Mtr | 100 | 101 | 10100
|  | Basic Total |  |  |  | 765582
|  | Freight |  |  |  | 0
|  | GST @ 18% |  |  |  | 137804.76
|  | TOTAL |  |  |  | 903386.76
Delivery
Note:
1. Payment terms: 50% advance and balance within seven days after completion of work.
2. Time line: One month after confirmation or receiving LOI/WO.
( DIPEN CHAKRABORTY )